## Settings
| Value | Unit | Range | Comment
Casegroup | RfG | -
Run custom cases | TRUE | - |  | If custom not selected for casegroup.
Projectname | Solbakken | -
Pn | 200 | MW
Uc | 161.9 | kV |  | Used for easy setup to make sure simulations, start in normal operation voltage and not 1 pu.
Un | 152 | kV |  | This will be 1pu in simulations and results |  | Western Denmark, DK1, CE |  |  | Eastern Denmark, DK2, N
Area | DK1 |  |  |  | Voltage level POC | 150 kV | 220 kV | 400kV | 132 kV | 220 kV | 400 kV
SCR min | 10 | - |  |  | 1 pu | 152 kV | 220 kV | 400kV | 138 kV | 234 kV | 400 kV
SCR tuning | 20 | -
SCR max | 30 | -
V droop | 2 | %
X/R SCR min | 20 | -
X/R SCR tuning | 15 | -
X/R SCR max | 10 | -
R0 | 0 | ohm |  | Grounding impedance of the MTB voltage source
X0 | 0 | ohm |  | Grounding impedance of the MTB voltage source
Default Q mode | Q | - |  | Qmode signal from MTB is constant. Qref mode == 0, Q(U) mode == 1 and Qpf == 2.
PSCAD Timestep | 2 | µs
PSCAD Initialization time | 3.5 | s |  | Atleast 1s
PF flat time | 0.1 | s |  | Atleast 0,1s
PF variable step | TRUE | -
PF enforced sync. | TRUE | -
PF force asymmetrical sim. | FALSE | -
PF enforce P limits in LDF | TRUE | - |  | Can be neccesary to turn off when QDSL is utilized for initialization.
PF enforce Q limits in LDF | TRUE | - |  | Can be neccesary to turn off when QDSL is utilized for initialization.

## Area values
| DK1 |  |  | DK2
Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | Selected
Power-frequency control
LFSM-O start (Hz) | 50.2 | 50.2 | 50.2 | 50.5 | 50.5 | 50.5 | 50.2
LFSM-O droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
LFSM-U start (Hz) | 49.8 | 49.8 | 49.8 | 49.5 | 49.5 | 49.5 | 49.8
LFSM-U droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
FSM deadband (Hz) | 0 | 0 | 0 | 0 | 0 | 0 | 0
FSM droop (%) | 6 | 6 | 6 | 6 | 6 | 6 | 6
FSM provision (%Pn) | 10 | 10 | 10 | 10 | 10 | 10 | 10
30min operation Fmax | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
30min operation Fmin | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Reactive power capability (base Uc)
UQ Q=0pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=0pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=+0.33pu Umax | 1.04 | 1.108 | 1.04 | 1.04 | 1.04 | 1.04 | 1.108
UQ Q=+0.33pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=-0.33pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=-0.33pu Umin | 0.96 | 1.028 | 0.96 | 0.96 | 0.96 | 0.96 | 1.028
Cont. operation Umax | 1.1 | 1.118 | 1.05 | 1.1 | 1.05 | 1.05 | 1.118
Cont. operation Umin | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
60min operation Umax | 1.1 | 1.15 | 1.1 | 1.1 | 1.1 | 1.1 | 1.15
60min operation Umin | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT
LVFT start | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT stop | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
Ures | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
tclear | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Uclear | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec1 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec1 | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec2 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec2 | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
trec3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
OVRT
U1 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3
t1 | 5 | 0.1 | 0.1 | 5 | 0.1 | 0.1 | 0.1
U2 | 1.15 | 1.2 | 1.2 | 1.15 | 1.2 | 1.2 | 1.2
t2 | 60 | 30 | 30 | 60 | 30 | 30 | 30

## RfG cases
|  |  | = Disabled for DSO cases | [8 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1 | TRUE | TRUE | ION_RfG_P_step_up_0.0_0.5 | 1.0651 | 0 | LFSM | Default | 0 | 10 | 20 | 155 | Pref | 0 | 0.5 | 0
2 | TRUE | TRUE | ION_RfG_P_step_up_0.5_0.7 | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 20 | 80 | Pref | 0 | 0.7 | 0
3 | TRUE | TRUE | ION_RfG_P_step_up_0.7_1.0 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 100 | Pref | 0 | 1 | 0
4 | TRUE | TRUE | ION_RfG_P_step_down_1.0_0.7 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 100 | Pref | 0 | 0.7 | 0
5 | TRUE | TRUE | ION_RfG_P_step_down_0.7_0.5 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 80 | Pref | 0 | 0.5 | 0
6 | TRUE | TRUE | ION_RfG_P_step_down_0.5_0.0 | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 20 | 155 | Pref | 0 | 0 | 0
7 | TRUE | TRUE | ION_RfG_FSM_step1 | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 20 | 60 | Frequency | 0 | 50.199 |  | Frequency | 15 | 50 |  | Frequency | 30 | 49.801 |  | Frequency | 45 | 50
8 | TRUE | TRUE | ION_RfG_FSM_step2 | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 20 | 60 | Frequency | 0 | 50.15 |  | Frequency | 15 | 50 |  | Frequency | 30 | 49.85 |  | Frequency | 45 | 50
9 | TRUE | TRUE | ION_RfG_LFSM-OU_step1 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
10 | TRUE | TRUE | ION_RfG_LFSM-O_ramp | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 21.5 | Frequency | 0 |  | 0.5 | Frequency | 3 | 51.5 | 0 | Frequency | 5 |  | -0.2 | Frequency | 11.5 | 50.2 | 0
11 | TRUE | TRUE | ION_RfG_LFSM-U_ramp | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 21.5 | Frequency | 0 |  | -0.5 | Frequency | 3 | 48.5 | 0 | Frequency | 5 |  | 0.2 | Frequency | 11.5 | 49.8 | 0
12 | TRUE | TRUE | ION_RfG_FSM_LFSM-O_ramp | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 20 | 26.5 | Frequency | 0 |  | 0.2 | Frequency | 7.5 | 51.5 | 0 | Frequency | 9 |  | -0.2 | Frequency | 16.5 | 50 | 0
13 | TRUE | TRUE | ION_RfG_FSM_LFSM-U_step | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 20 | 45 | Frequency | 0 | 49.8 |  | Frequency | 5 | 49.5 |  | Frequency | 10 | 49.8 |  | Frequency | 15 | 49.85 |  | Frequency | 25 | 49.5 |  | Frequency | 35 | 50
14 | TRUE | TRUE | ION_RfG_U-Q/Pn_Neutral | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 | 80 | Voltage | 0 | 1.118 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 0.968 |  | Voltage | 60 | 1.0651
15 | TRUE | TRUE | ION_RfG_U-Q/Pn_Neutral_stab | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 80 | dVoltage | 0 | 0.052868 |  | dVoltage | 20 | 0 |  | dVoltage | 40 | -0.097132 |  | dVoltage | 60 | 0
16 | TRUE | TRUE | ION_RfG_U-Q/Pn_underEX | 1.0651 | 1 | LFSM | Q | -0.33 | -1 | 0 | 80 | Voltage | 0 | 1.118 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 1.028 |  | Voltage | 60 | 1.0651
17 | TRUE | TRUE | ION_RfG_U-Q/Pn_overEX | 1.0651 | 1 | LFSM | Q | 0.33 | -1 | 0 | 80 | Voltage | 0 | 1.108 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 0.968 |  | Voltage | 60 | 1.0651
18 | TRUE | TRUE | ION_RfG_PQ/Pn_Neutral1 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 155 | Pref | 0 | 0.5
19 | TRUE | TRUE | ION_RfG_PQ/Pn_Neutral2 | 1.0651 | 0.5 | LFSM | Q | 0 | 10 | 20 | 155 | Pref | 0 | 0
20 | TRUE | TRUE | ION_RfG_PQ/Pn_underEX1 | 1.0651 | 1 | LFSM | Q | -0.33 | 10 | 20 | 155 | Pref | 0 | 0.5
21 | TRUE | TRUE | ION_RfG_PQ/Pn_underEX2 | 1.0651 | 0.5 | LFSM | Q | -0.33 | 10 | 20 | 155 | Pref | 0 | 0
22 | TRUE | TRUE | ION_RfG_PQ/Pn_overEX1 | 1.0651 | 1 | LFSM | Q | 0.33 | 10 | 20 | 155 | Pref | 0 | 0.5
23 | TRUE | TRUE | ION_RfG_PQ/Pn_overEX2 | 1.0651 | 0.5 | LFSM | Q | 0.33 | 10 | 20 | 155 | Pref | 0 | 0
24 | TRUE | TRUE | ION_RfG_Ucontrol_Scmin | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 85 | dVoltage | 0 | 0.010651 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.010651 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.021303 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.021303 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
25 | TRUE | TRUE | ION_RfG_Ucontrol_Sctune | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 20 | 15 | 85 | dVoltage | 0 | 0.010651 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.010651 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.021303 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.021303 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
26 | TRUE | TRUE | ION_RfG_Ucontrol_Scmax | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 30 | 10 | 85 | dVoltage | 0 | 0.010651 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.010651 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.021303 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.021303 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
27 | TRUE | TRUE | ION_RfG_Uarea_Qreq_1(up) | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 1.118
28 | TRUE | TRUE | ION_RfG_Uarea_Qreq_2(up) | 1.118 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 1.15
29 | TRUE | TRUE | ION_RfG_Uarea_Qreq_1(down) | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.968
30 | TRUE | TRUE | ION_RfG_Uarea_Qreq_2(down) | 0.968 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.9
31 | TRUE | TRUE | ION_RfG_Uarea_Qreq_3(down) | 0.9 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.85
32 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_1(up) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 1.118
33 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_2(up) | 1.118 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 1.15
34 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_1(down) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 0.968
35 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_2(down) | 0.968 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 0.9
36 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_3(down) | 0.9 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 0.85
37 | TRUE | TRUE | ION_RfG_Q_control_up | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 120 | Qref | 0 | 0.1 |  | Qref | 30 | 0.2 |  | Qref | 60 | 0.33 |  | Qref | 90 | 0
38 | TRUE | TRUE | ION_RfG_Q_control_down | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 120 | Qref | 0 | -0.1 |  | Qref | 30 | -0.2 |  | Qref | 60 | -0.33 |  | Qref | 90 | 0
39 | TRUE | TRUE | ION_RfG_Qpf_Pfref-change | 1.0651 | 1 | LFSM | PF | 1 | 10 | 20 | 120 | Qref | 0 | 0.95 |  | Qref | 30 | 1 |  | Qref | 60 | -0.95 |  | Qref | 90 | 1
40 | TRUE | TRUE | ION_RfG_Qpf_P-change | 1.0651 | 0.3 | LFSM | PF | 0.99 | 10 | 20 | 135 | Pref | 0 | 0.4 |  | Pref | 35 | 0.5 |  | Pref | 70 | 0.6 |  | Pref | 100 | 0.7
41 | TRUE | TRUE | ION_RfG_SystemGuard | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 45 | Signal 1 | -1 | 1 |  | Signal 1 | 0 | 0.5 |  | Signal 1 | 15 | 0.25 |  | Signal 1 | 30 | 1
42 | TRUE | TRUE | ION_RfG_MaxPhaseJump | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
43 | TRUE | TRUE | ION_RfG_MaxPhaseJump2 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
44 | TRUE | TRUE | ION_RfG_MaxRoCoF1 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 10 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
45 | TRUE | TRUE | ION_RfG_MaxRoCoF2 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 5 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 | 50 | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
46 | TRUE | TRUE | ION_RfG_MaxRoCoF_CurveOF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
47 | TRUE | TRUE | ION_RfG_MaxRoCoF_CurveUF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
48 | TRUE | TRUE | ION_RfG_LVFRT_profile | 1.0651 | 1 | LFSM | Default | 0 | -1 | 0 | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0
49 | TRUE | TRUE | ION_RfG_OVRT_profile | 1.0651 | 1 | LFSM | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 30 | 1.15
50 | TRUE | TRUE | ION_RfG_Fault_3_0 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 0% | 0.15
51 | TRUE | TRUE | ION_RfG_Fault_3_20 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 20% | 0.45
52 | TRUE | TRUE | ION_RfG_Fault_3_40 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 40% | 0.75
53 | TRUE | TRUE | ION_RfG_Fault_3_80 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 80% | 1.35
54 | TRUE | TRUE | ION_RfG_Fault_3_thres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 85% | 1.35
55 | TRUE | TRUE | ION_RfG_Fault_2_0 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 0% | 0.15
56 | TRUE | TRUE | ION_RfG_Fault_2_20 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 20% | 0.45
57 | TRUE | TRUE | ION_RfG_Fault_2_40 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 40% | 0.75
58 | TRUE | TRUE | ION_RfG_Fault_2_80 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 80% | 1.35
59 | TRUE | TRUE | ION_RfG_Fault_2_thres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 85% | 1.35
60 | TRUE | TRUE | ION_RfG_Fault_1_0 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 0% | 0.15
61 | TRUE | TRUE | ION_RfG_Fault_1_20 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 20% | 0.45
62 | TRUE | TRUE | ION_RfG_Fault_1_40 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 40% | 0.75
63 | TRUE | TRUE | ION_RfG_Fault_1_80 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 80% | 1.35
64 | TRUE | TRUE | ION_RfG_Fault_1_thres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 85% | 1.35
65 | TRUE | TRUE | ION_RfG_Voltage-support | 1.0651 | 1 | LFSM | Default | 0 | -1 | 0 | 5 | Voltage | 0 | 0.7 |  | Voltage | 0.2 | 0.5 |  | Voltage | 0.4 | 0.3 |  | Voltage | 0.6 | 1
66 | TRUE | TRUE | ION_RfG_Fault_1_restrike | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
67 | TRUE | TRUE | ION_RfG_Fault_3_double | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
68 | TRUE | TRUE | ION_RfG_Fault_2_double | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
69 | TRUE | TRUE | ION_RfG_Fault_3_SCR | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 20
70 | TRUE | TRUE | ION_RfG_Fault_2_SCR | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 20
71 | TRUE | TRUE | EXT_SS_flatrun_Q1 | 1.0651 | 0 | LFSM | Q | 0 | 10 | 20 | 60 | PF disconnect all ref.
72 | TRUE | TRUE | EXT_SS_flatrun_Q2 | 1.0651 | 0.5 | LFSM | Q | 0.2 | 10 | 20 | 60 | PF disconnect all ref.
73 | TRUE | TRUE | EXT_SS_flatrun_Q3 | 1.0651 | 0.5 | LFSM | Q | -0.2 | 10 | 20 | 60 | PF disconnect all ref.
74 | TRUE | TRUE | EXT_SS_flatrun_Q4 | 1.0651 | 1 | LFSM | Q | 0.33 | 10 | 20 | 60 | PF disconnect all ref.
75 | TRUE | TRUE | EXT_SS_flatrun_Q5 | 1.0651 | 1 | LFSM | Q | -0.33 | 10 | 20 | 60 | PF disconnect all ref.
76 | TRUE | TRUE | EXT_SS_flatrun_Q6 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | PF disconnect all ref.
77 | TRUE | TRUE | EXT_SS_flatrun_Uctrl1 | 0.968 | 0.7 | LFSM | Q(U) | 1.0651 | -1 | 0 | 60 | PF disconnect all ref.
78 | TRUE | TRUE | EXT_SS_flatrun_Uctrl2 | 1.118 | 0.7 | LFSM | Q(U) | 1.0651 | -1 | 0 | 60 | PF disconnect all ref.
79 | TRUE | TRUE | EXT_SS_flatrun_PFctrl1 | 1.0651 | 0.7 | LFSM | PF | 0.949 | 10 | 20 | 60 | PF disconnect all ref.
80 | TRUE | TRUE | EXT_SS_flatrun_PFctrl2 | 1.0651 | 0.7 | LFSM | PF | -0.949 | 10 | 20 | 60 | PF disconnect all ref.
81 | TRUE | TRUE | EXT_RfG_LFSM-OU_step2 | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 20 | 160 | Frequency | 0 | 50.825 |  | Frequency | 20 | 50 |  | Frequency | 40 | 49.175 |  | Frequency | 60 | 50 |  | Frequency | 80 | 51.45 |  | Frequency | 100 | 50 |  | Frequency | 120 | 48.55 |  | Frequency | 140 | 50
82 | TRUE | TRUE | EXT_RfG_LFSM-OU_step1+FSM | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 20 | 80 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 50
83 | TRUE | TRUE | EXT_RfG_FSM_rec_pstep | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 20 |  | Frequency recording |  | recordings/DK1_frekvens.meas | 1 | Pref | 1 | 0 | 0
84 | TRUE | TRUE | EXT_RfG_LFSMO_ramp+pstep | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 20 | 40 | Frequency | 0 |  | 0.075 | Frequency | 15 |  | 0 | Pref | 0.1 | 1 |  | Frequency | 20 | 50
85 | TRUE | TRUE | EXT_RfG_LFSM-O_Plimited | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 50 | Signal 2 | -1 | 0.5 |  | Frequency | 10 | 51 |  | Frequency | 30 | 50
86 | TRUE | TRUE | EXT_RfG_LFSM-U_Plimited | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 20 | 30 | Signal 2 | -1 | 0.8 |  | Frequency | 5 | 48.5 |  | Frequency | 20 | 50
87 | TRUE | TRUE | EXT_RfG_LFSM-O_Q_control | 1.0651 | 0.7 | LFSM | Q | 0.1 | 10 | 20 | 40 | Qref | 0 | 0.25 |  | Frequency | 1 | 51 |  | Frequency | 25 | 50 |  | Qref | 27 | 0.1
88 | TRUE | TRUE | EXT_RfG_Ucontrol_LFSM-O | 1.0651 | 0.7 | LFSM | Q(U) | 1.0651 | 10 | 20 | 15 | dVoltage | 0 | -0.1 |  | Frequency | 0.5 |  | 1 | Frequency | 1.5 | 51 | 0 | Frequency | 3.5 |  | -0.5 | Frequency | 5.5 | 50 | 0 | dVoltage | 5 | 0
89 | TRUE | TRUE | EXT_RfG_Ucontrol_FRTsensitivity | 1 | 1 | LFSM | Q(U) | 1 | -1 | 0 | 50 | Voltage | 2 | 0.85 |  | Voltage | 7 | 0.84 |  | Voltage | 12 | 1 | 0 | Voltage | 20 | 0.84 |  | Voltage | 25 | 1 |  | Voltage | 32 | 0.87 |  | Voltage | 37 | 0.83 |  | Voltage | 42 | 1
90 | TRUE | TRUE | EXT_RfG_Pavail_variation | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 20 | Signal 2 | -1 | 1 |  | Signal 2 | 1 | 0.75 |  | Signal 2 | 5 | 0.25 |  | Signal 2 | 10 | 1
91 | TRUE | TRUE | EXT_RfG_MaxPhaseJump_Extreme | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 10 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | -40 |  | Phase | 7.5 | 0
92 | TRUE | TRUE | EXT_RfG_RoCoF_ACER-CurveOF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | 4 | Frequency | 0.25 |  | 1.3333 | Frequency | 1 |  | 0.33333 | Frequency | 2.5 |  | 0 | Frequency | 4.5 |  | -1 | Frequency | 5.5 |  | 0
93 | TRUE | TRUE | EXT_RfG_RoCoF_ACER-CurveUF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | -4 | Frequency | 0.25 |  | -1.33 | Frequency | 1 |  | -0.333 | Frequency | 2.5 |  | 0 | Frequency | 4.5 |  | 1 | Frequency | 6 |  | 0
94 | TRUE | TRUE | EXT_RfG_RoCoF+PhaseJump1 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 5 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | -20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
95 | TRUE | TRUE | EXT_RfG_RoCoF+PhaseJump2 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 20 | 5 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | 20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
96 | TRUE | TRUE | EXT_RfG_Fault_3_0_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 3p fault | 0 | 0% | 0.15
97 | TRUE | TRUE | EXT_RfG_Fault_3_20_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 3p fault | 0 | 20% | 0.45
98 | TRUE | TRUE | EXT_RfG_Fault_3_40_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 3p fault | 0 | 40% | 0.75
99 | TRUE | TRUE | EXT_RfG_Fault_3_80_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 3p fault | 0 | 80% | 1.35
100 | TRUE | TRUE | EXT_RfG_Fault_3_thres_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 3p fault | 0 | 85% | 1.35
101 | TRUE | TRUE | EXT_RfG_Fault_3_UnderThres_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 3p fault | 0 | 83% | 1.35
102 | TRUE | TRUE | EXT_RfG_Fault_3_UnderThres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 83% | 1.35
103 | TRUE | TRUE | EXT_RfG_Fault_2_20_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 2p-g fault | 0 | 20% | 0.45
104 | TRUE | TRUE | EXT_RfG_Fault_2_40_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 | 12 | 2p-g fault | 0 | 40% | 0.75
105 | TRUE | TRUE | EXT_RfG_Fault_3_SCR_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 20 | 15 | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 20
106 | TRUE | TRUE | EXT_RfG_Fault_2_SCR_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 20 | 15 | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 20
107 | TRUE | TRUE | EXT_RfG_Fault_3_20_short | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 2 | 3p fault | 0 | 20% | 0.25
108 | TRUE | TRUE | EXT_RfG_Fault_2_20_short | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 2 | 2p-g fault | 0 | 20% | 0.25
109 | TRUE | TRUE | EXT_RfG_Fault_3_20_WG | 1.0651 | 1 | LFSM | Default | 0 | 2 | 3 | 12 | 3p fault | 0 | 20% | 0.2
110 | TRUE | TRUE | EXT_RfG_Fault_2_20_WG | 1.0651 | 1 | LFSM | Default | 0 | 2 | 3 | 12 | 2p-g fault | 0 | 20% | 0.2
111 | TRUE | TRUE | EXT_RfG_Fault_3_ROCOF_curveOF | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 15 | 3p fault | 0 | 40% | 0.2 | Frequency | 1.21 |  | 4 | Frequency | 1.26 |  | 2 | Frequency | 1.36 |  | 1 | Frequency | 2.11 |  | 0.35 | Frequency | 3.11 |  | 0 | Frequency | 5.11 |  | -1 | Frequency | 6.11 |  | 0
112 | TRUE | TRUE | EXT_RfG_Fault_3_ROCOF_curveUF | 1.0651 | 1 | LFSM | Default | 0 | 10 | 20 | 15 | 3p fault | 0 | 40% | 0.2 | Frequency | 1.21 |  | -4 | Frequency | 1.26 |  | -2 | Frequency | 1.36 |  | -1 | Frequency | 2.11 |  | -0.35 | Frequency | 3.11 |  | 0 | Frequency | 5.11 |  | 1 | Frequency | 6.11 |  | 0
113 | TRUE | TRUE | EXT_RfG_Fault_3_SCR_freqStep1 | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 20 | Frequency | 0.205 | 51 |  | Frequency | 6 | 50
114 | TRUE | TRUE | EXT_RfG_Fault_3_SCR_freqStep2 | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 20 | Frequency | 0.205 | 51 |  | Frequency | 4 | 50
115 | TRUE | TRUE | EXT_SCR_step_Max-Min | 1.0651 | 1 | LFSM | Default | 0 | 30 | 10 | 10 | SCR | 0 | 10 | 20 | SCR | 5 | 30 | 10
116 | TRUE | TRUE | EXT_SCR_step_Max-Min_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 30 | 10 | 10 | SCR | 0 | 10 | 20 | SCR | 5 | 30 | 10
117 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
118 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q(U) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
119 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q_SCmin | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
120 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q(U)_SCmin | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 20 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
121 | TRUE | TRUE | EXT_RfG_Fault_rec_2_Q | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault2.meas | 1.0651
122 | TRUE | TRUE | EXT_RfG_Fault_rec_2_Q(U) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault2.meas | 1.0651
123 | TRUE | TRUE | EXT_RfG_Fault_rec_3_Q | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
124 | TRUE | TRUE | EXT_RfG_Fault_rec_3_Q(U) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
125 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.2 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.2 | 0
126 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.3 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.3 | 0
127 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.4 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.4 | 0
128 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.5 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.5 | 0
129 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_insta_min | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 7 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
130 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_insta_max | 1.0651 | 1 | LFSM | Q | 0 | 30 | 10 | 7 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
131 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.8pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | 3p fault | 0 | 80% | 60
132 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.6pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | 3p fault | 0 | 60% | 60
133 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.40pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | 3p fault | 0 | 40% | 60
134 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.20pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 20 | 60 | 3p fault | 0 | 20% | 60
135 | TRUE | TRUE | EXT_RfG_proc_Freq_51.6Hz | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 20 | 60 | Frequency | 0 | 51.6
136 | TRUE | TRUE | EXT_RfG_proc_Freq_47.4Hz | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 20 | 60 | Frequency | 0 | 47.4
137 | TRUE | TRUE | EXT_RfG_proc_Freq_limit_up | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 20 | 40 | Frequency | 0 | 52 |  | Frequency | 8 | 53 |  | Frequency | 16 | 54 |  | Frequency | 24 | 55 |  | Frequency | 32 | 56 |  | Frequency | 35 | 50
138 | TRUE | TRUE | EXT_RfG_proc_Freq_limi_down | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 20 | 40 | Frequency | 0 | 47 |  | Frequency | 8 | 46 |  | Frequency | 16 | 45 |  | Frequency | 24 | 44 |  | Frequency | 32 | 43 |  | Frequency | 35 | 50
139 | TRUE | TRUE | EXT_RfG_proc_Fault_1_0.05pu | 1.0651 | 1 | LFSM | Q | 0 | 30 | 20 | 60 | 1p fault | 0 | 5% | 60

## DCC cases
|  |  | DSO plants only RfG cases and deactive coloured. | [8 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1001 | TRUE | TRUE | DCC_Fault_3_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 0% | 0.15
1002 | TRUE | TRUE | DCC_Fault_3_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 20% | 0.45
1003 | TRUE | TRUE | DCC_Fault_3_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 40% | 0.75
1004 | TRUE | TRUE | DCC_Fault_3_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 80% | 1.35
1005 | TRUE | TRUE | DCC_Fault_2_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 0% | 0.15
1006 | TRUE | TRUE | DCC_Fault_2_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 20% | 0.45
1007 | TRUE | TRUE | DCC_Fault_2_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 40% | 0.75
1008 | TRUE | TRUE | DCC_Fault_2_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 80% | 1.35
1009 | TRUE | TRUE | DCC_Fault_1_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 0% | 0.15
1010 | TRUE | TRUE | DCC_Fault_1_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 20% | 0.45
1011 | TRUE | TRUE | DCC_Fault_1_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 40% | 0.75
1012 | TRUE | TRUE | DCC_Fault_1_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 80% | 1.35
1013 | TRUE | TRUE | DCC_Fault_3_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 20
1014 | TRUE | TRUE | DCC_Fault_2_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 20
1015 | TRUE | TRUE | DCC_SCR_step_Max-Min | 1.0651 | 1 | No P(f) | Default | 0 | 30 | 10 | 10 | SCR | 0 | 10 | 20 | SCR | 5 | 30 | 10
1016 | TRUE | TRUE | DCC_HVRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 30 | Voltage | 0 | 1.15 | 0 | Voltage | 10 | 1.2 | 0 | Voltage | 17 | 1.3 | 0 | Voltage | 25 | 1
1017 | TRUE | TRUE | DCC_UVRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 45 | Voltage | 0 | 0.9 |  | Voltage | 10 | 0.85 |  | Voltage | 17 | 0.8 |  | Voltage | 25 | 0.7 |  | Voltage | 32 | 0.6 |  | Voltage | 37 | 1
1018 | TRUE | TRUE | DCC_SystemGuard | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 45 | Signal 1 | -1 | 1 |  | Signal 1 | 0 | 0.5 |  | Signal 1 | 15 | 0.25 |  | Signal 1 | 30 | 1
1019 | TRUE | TRUE | DCC_MaxPhaseJump | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
1020 | TRUE | TRUE | DCC_MaxPhaseJump2 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
1021 | TRUE | TRUE | DCC_MaxRoCoF1 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
1022 | TRUE | TRUE | DCC_MaxRoCoF2 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 5 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 | 50 | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
1023 | TRUE | TRUE | DCC_MaxRoCoF_CurveOF | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
1024 | TRUE | TRUE | DCC_MaxRoCoF_CurveUF | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
1025 | TRUE | TRUE | DCC_LFSM-OU_step1 | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
1026 | TRUE | TRUE | DCC_LFSM-O_ramp | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 21.5 | Frequency | 0 |  | 0.5 | Frequency | 3 | 51.5 | 0 | Frequency | 5 |  | -0.2 | Frequency | 11.5 | 50.2 | 0
1027 | TRUE | TRUE | DCC_LFSM-U_ramp | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 21.5 | Frequency | 0 |  | -0.5 | Frequency | 3 | 48.5 | 0 | Frequency | 5 |  | 0.2 | Frequency | 11.5 | 49.8 | 0
1028 | TRUE | TRUE | DCC_LFDD | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | Frequency | 0 | 48.9 |  | Frequency | 10 | 48.8 |  | Frequency | 20 | 48.6 |  | Frequency | 30 | 48.4 |  | Frequency | 40 | 48.2 |  | Frequency | 50 | 50
1029 | TRUE | TRUE | DCC_Faera-O | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | Frequency | 0 | 50.5 |  | Frequency | 10 | 51 |  | Frequency | 20 | 51.5 |  | Frequency | 30 | 52 |  | Frequency | 40 | 53 |  | Frequency | 50 | 50
1030 | TRUE | TRUE | DCC_Faera-U | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 70 | Frequency | 0 | 49.5 |  | Frequency | 10 | 49 |  | Frequency | 20 | 48 |  | Frequency | 30 | 47.5 |  | Frequency | 40 | 47 |  | Frequency | 50 | 46.5 |  | Frequency | 60 | 50
1031 | TRUE | TRUE | DCC_Uarea_Qreq_1(up) | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.118
1032 | TRUE | TRUE | DCC_Uarea_Qreq_2(up) | 1.118 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.15
1033 | TRUE | TRUE | DCC_Uarea_Qreq_1(down) | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 0.968
1034 | TRUE | TRUE | DCC_Uarea_Qreq_2(down) | 0.968 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 0.9
1035 | TRUE | TRUE | DCC_Uarea_Qreq_3(down) | 0.9 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 0.85
1036 | TRUE | TRUE | DCC_VoltageRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.05 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.05 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.05 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.05 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.05 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.05 | 1
1037 | TRUE | TRUE | DCC_VoltageDip_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Voltage | 0 | 0.9 | 0 | Voltage | 0.05 | 1 |  | Voltage | 1 | 0.85 |  | Voltage | 1.05 | 1 |  | Voltage | 2 | 0.8 |  | Voltage | 2.05 | 1 |  | Voltage | 3 | 0.75 |  | Voltage | 3.05 | 1 |  | Voltage | 4 | 0.7 |  | Voltage | 4.05 | 1 |  | Voltage | 5 | 0.65 |  | Voltage | 5.05 | 1
1038 | TRUE | TRUE | DCC_freqRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 | 52 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 52.5 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 53 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 55 |  | Frequency | 3.05 | 50 |  | Frequency | 4 | 60 |  | Frequency | 4.05 | 50 |  | Frequency | 5 | 65 |  | Frequency | 5.05 | 50
1039 | TRUE | TRUE | DCC_freqDip_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 | 47.5 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 47 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 46.5 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 46 |  | Frequency | 3.05 | 50

## Unit cases
[12 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
2001 | TRUE | TRUE | UNT_SS_flatrun_Q1 | 1.0651 | 0 | No P(f) | Default | 0 | 10 | 20 | 60 | PF disconnect all ref.
2002 | TRUE | TRUE | UNT_SS_flatrun_Q2 | 1.0651 | 0.5 | No P(f) | Default | 0.2 | 10 | 20 | 60 | PF disconnect all ref.
2003 | TRUE | TRUE | UNT_SS_flatrun_Q3 | 1.0651 | 0.5 | No P(f) | Default | -0.2 | 10 | 20 | 60 | PF disconnect all ref.
2004 | TRUE | TRUE | UNT_SS_flatrun_Q4 | 1.0651 | 1 | No P(f) | Default | 0.33 | 10 | 20 | 60 | PF disconnect all ref.
2005 | TRUE | TRUE | UNT_SS_flatrun_Q5 | 1.0651 | 1 | No P(f) | Default | -0.33 | 10 | 20 | 60 | PF disconnect all ref.
2006 | TRUE | TRUE | UNT_SS_flatrun_Q6 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | PF disconnect all ref.
2007 | TRUE | TRUE | UNT_P_step_up_0.5_0.7 | 1.0651 | 0.5 | No P(f) | Default | 0 | 10 | 20 | 20 | Pref | 0 | 0.7 | 0 | Pref | 10 | 0.5
2008 | TRUE | TRUE | UNT_Q_control_up | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 20 | Qref | 0 | 0.1 |  | Qref | 5 | 0.2 |  | Qref | 10 | -0.1 |  | Qref | 15 | 0
2009 | TRUE | TRUE | UNT_U-Q/Pn_Neutral | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 20 | Voltage | 0 | 1.118 |  | Voltage | 5 | 1.0651 |  | Voltage | 10 | 0.968 |  | Voltage | 15 | 1.0651
2010 | TRUE | TRUE | UNT_fArea | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
2011 | TRUE | TRUE | UNT_LVFRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0
2012 | TRUE | TRUE | UNT_OVRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 30 | 1.15
2013 | TRUE | TRUE | UNT_Fault_3_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 0% | 0.15
2014 | TRUE | TRUE | UNT_Fault_3_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 20% | 0.45
2015 | TRUE | TRUE | UNT_Fault_3_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 40% | 0.75
2016 | TRUE | TRUE | UNT_Fault_3_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 3p fault | 0 | 80% | 1.35
2017 | TRUE | TRUE | UNT_Fault_2_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 0% | 0.15
2018 | TRUE | TRUE | UNT_Fault_2_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 20% | 0.45
2019 | TRUE | TRUE | UNT_Fault_2_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 40% | 0.75
2020 | TRUE | TRUE | UNT_Fault_2_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 2p-g fault | 0 | 80% | 1.35
2021 | TRUE | TRUE | UNT_Fault_1_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 0% | 0.15
2022 | TRUE | TRUE | UNT_Fault_1_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 20% | 0.45
2023 | TRUE | TRUE | UNT_Fault_1_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 40% | 0.75
2024 | TRUE | TRUE | UNT_Fault_1_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 12 | 1p fault | 0 | 80% | 1.35
2025 | TRUE | TRUE | UNT_Voltage-support | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 5 | Voltage | 0 | 70% |  | Voltage | 0.2 | 0.5 |  | Voltage | 0.4 | 0.3 |  | Voltage | 0.6 | 1
2026 | TRUE | TRUE | UNT_Fault_1_restrike | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
2027 | TRUE | TRUE | UNT_Fault_3_double | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
2028 | TRUE | TRUE | UNT_Fault_2_double | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
2029 | TRUE | TRUE | UNT_Fault_3_20_short | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 2 | 3p fault | 0 | 20% | 0.25 | SCR | 0.249 | 10 | 20
2030 | TRUE | TRUE | UNT_Fault_2_20_short | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 2 | 2p-g fault | 0 | 20% | 0.25
2031 | TRUE | TRUE | UNT_Fault_3_20_WG | 1.0651 | 1 | No P(f) | Default | 0 | 2 | 3 | 12 | 3p fault | 0 | 20% | 0.2
2032 | TRUE | TRUE | UNT_Fault_2_20_WG | 1.0651 | 1 | No P(f) | Default | 0 | 2 | 3 | 12 | 2p-g fault | 0 | 20% | 0.2
2033 | TRUE | TRUE | UNT_Fault_3_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 20
2034 | TRUE | TRUE | UNT_Fault_2_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 20
2035 | TRUE | TRUE | UNT_Fault_3_SCR_freqStep | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 20 | Frequency | 0.205 | 51 |  | Frequency | 5.5 | 50
2036 | TRUE | TRUE | Unit_SCR_step_Max-Min | 1.0651 | 1 | No P(f) | Default | 0 | 30 | 10 | 10 | SCR | 0 | 10 | 20 | SCR | 5 | 30 | 10
2037 | TRUE | TRUE | UNT_MaxPhaseJump | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
2038 | TRUE | TRUE | UNT_MaxPhaseJump2 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
2039 | TRUE | TRUE | UNT_MaxRoCoF_CurveOF | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
2040 | TRUE | TRUE | UNT_MaxRoCoF_CurveUF | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
2041 | TRUE | TRUE | UNT_MaxPhaseJump_Extreme_min | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
2042 | TRUE | TRUE | UNT_MaxPhaseJump_Extreme_max | 1.0651 | 1 | No P(f) | Default | 0 | 30 | 10 | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
2043 | TRUE | TRUE | UNT_VoltageRise_1.2 | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.2 | 0
2044 | TRUE | TRUE | UNT_VoltageRise_1.3 | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.3 | 0
2045 | TRUE | TRUE | UNT_VoltageRise_1.4 | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.4 | 0
2046 | TRUE | TRUE | UNT_VoltageRise_1.5 | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | dVoltage | 0 | 0.5 | 0
2047 | TRUE | TRUE | UNT_VoltageRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
2048 | TRUE | TRUE | UNT_VoltageRise_insta_max | 1 | 1 | No P(f) | Default | 0 | 30 | 10 | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
2049 | TRUE | TRUE | Unit_freqRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 | 52 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 52.5 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 53 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 55 |  | Frequency | 3.05 | 50 |  | Frequency | 4 | 60 |  | Frequency | 4.05 | 50 |  | Frequency | 5 | 65 |  | Frequency | 5.05 | 50
2050 | TRUE | TRUE | Unit_freqDip_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 10 | Frequency | 0 | 47.5 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 47 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 46.5 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 46 |  | Frequency | 3.05 | 50
2051 | TRUE | TRUE | UNT_prot_Fault_3_0.8pu | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | 3p fault | 0 | 80% | 60
2052 | TRUE | TRUE | UNT_prot_Fault_3_0.6pu | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | 3p fault | 0 | 60% | 60
2053 | TRUE | TRUE | UNT_prot_Fault_3_0.40pu | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | 3p fault | 0 | 40% | 60
2054 | TRUE | TRUE | UNT_prot_Fault_3_0.20pu | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | 3p fault | 0 | 20% | 60
2055 | TRUE | TRUE | UNT_prot_Fault_1_0.05pu | 1 | 1 | No P(f) | Default | 0 | 10 | 20 | 60 | 1p fault | 0 | 5% | 60
2056 | TRUE | TRUE | UNT_Freq_53Hz | 1 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 60 | Frequency | 0 | 53
2057 | TRUE | TRUE | UNT_Freq_46Hz | 1 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 60 | Frequency | 0 | 46
2058 | TRUE | TRUE | UNT_Freq_limit_up | 1 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 30 | Frequency | 0 | 52 |  | Frequency | 5 | 53 |  | Frequency | 10 | 54 |  | Frequency | 15 | 55 |  | Frequency | 20 | 56 |  | Frequency | 25 | 50
2059 | TRUE | TRUE | UNT_Freq_limi_down | 1 | 0.7 | No P(f) | Default | 0 | 10 | 20 | 30 | Frequency | 0 | 47 |  | Frequency | 5 | 46 |  | Frequency | 10 | 45 |  | Frequency | 15 | 44 |  | Frequency | 20 | 43 |  | Frequency | 25 | 50
2060 | FALSE | TRUE | UNT_Pavail_variation | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 20 | 20 | Signal 2 | 1 | 0.75 |  | Signal 2 | 5 | 0.25 |  | Signal 2 | 10 | 1

## Custom cases
[12 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
3001 | TRUE | FALSE | Custom_1 | 1.0651 | 1 | No P(f) | Qmode3 | 0 | 30 | 10 | 5 | 3p fault | 0.1 | 5% | 0.1 | Qref | 1 | 0.1

## Event types
Name | Description | X1 description | X1 unit | X2 description | X2 unit
Pref | Pref change | setpoint, base Pn | pu | gradient | 1/s
Qref | Qref change | setpoint, base Pn | pu | gradient | 1/s
Voltage | Grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
dVoltage | Delta grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
Phase | Grid phase change (thevenin) | setpoint | degree | gradient | degree/s
Frequency | Grid frequency change | setpoint | Hz | gradient | Hz/s
SCR | Grid impedance change | SCR | - | X/R | -
3p fault | Three phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p-g fault | Two phase to ground fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p fault | Two phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
1p fault | One phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
3p fault (ohm) | Three phase fault | fault resistance | ohm | fault reactance | ohm
2p-g fault (ohm) | Two phase to ground fault | fault resistance | ohm | fault reactance | ohm
2p fault (ohm) | Two phase fault | fault resistance | ohm | fault reactance | ohm
1p fault (ohm) | One phase fault | fault resistance | ohm | fault reactance | ohm
Clear fault | Clear any fault | N/A | N/A | N/A | N/A
Pref recording | Use external measurement file for Pref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Qref recording | Use external measurement file for Qref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Voltage recording | Use external measurement file for the thevenin voltage signal (RMS). First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Inst. Voltage recording | Only supported for PSCAD. Use external measurement file for the thevenin instantaneous voltages. Time value ignored. | Relative path to measurementfile | N/A | Scaling factor | -
Phase recording | Use external measurement file for the thevenin voltage phase signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Frequency recording | Use external measurement file for the thevenin voltage frequency signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 1 | Custom signal 1 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 2 | Custom signal 2 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 3 | Custom signal 3 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 4 | Custom signal 4 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 5 | Custom signal 5 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 6 | Custom signal 6 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 7 | Custom signal 7 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 8 | Custom signal 8 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 9 | Custom signal 9 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 10 | Custom signal 10 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 1 recording | Use external measurement file for custom signal 1. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 2 recording | Use external measurement file for custom signal 2. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 3 recording | Use external measurement file for custom signal 3. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 4 recording | Use external measurement file for custom signal 4. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 5 recording | Use external measurement file for custom signal 5. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 6 recording | Use external measurement file for custom signal 6. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 7 recording | Use external measurement file for custom signal 7. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 8 recording | Use external measurement file for custom signal 8. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 9 recording | Use external measurement file for custom signal 9. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 10 recording | Use external measurement file for custom signal 10. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
PF disconnect all ref. | In Powerfactory out-of-service all references (including custom signals) to plant. For initialization testing purposes. | N/A | N/A | N/A | N/A
PF force asymmetrical | Force case to be simulated asymmetricaly. | N/A | N/A | N/A | N/A

## datavalidation (hidden)
DK1 | Q | No P(f) | Max | TRUE | RfG
DK2 | Q(U) | LFSM | Min | FALSE | DCC
| PF | FSM | Tuning |  | Unit
| Default | LFSM+FSM | Ideal |  | Custom
| Qmode3 | Pmode4
| Qmode4 | Pmode5
| Qmode5 | Pmode6
| Qmode6 | Pmode7