## Settings
| Value | Unit | Range | Comment
Casegroup | RfG | -
Run custom cases | TRUE | - |  | If custom not selected for casegroup.
Projectname | Solbakken | -
Pn | 200 | MW
Uc | 161.9 | kV |  | Used for easy setup to make sure simulations, start in normal operation voltage and not 1 pu.
Un | 152 | kV |  | This will be 1pu in simulations and results |  | Western Denmark, DK1, CE |  |  | Eastern Denmark, DK2, N
Area | DK1 |  |  |  | Voltage level POC | 150 kV | 220 kV | 400kV | 132 kV | 220 kV | 400 kV
SCR min | 10 | - |  |  | 1 pu | 152 kV | 220 kV | 400kV | 138 kV | 234 kV | 400 kV
SCR tuning | 20 | -
SCR max | 30 | -
V droop | 2 | %
X/R SCR min | 10 | -
X/R SCR tuning | 15 | -
X/R SCR max | 20 | -
R0 | 0 | ohm |  | Grounding impedance of the MTB voltage source
X0 | 0 | ohm |  | Grounding impedance of the MTB voltage source
Default Q mode | Q | - |  | Qmode signal from MTB is constant. Qref mode == 0, Q(U) mode == 1 and Qpf == 2.
PSCAD Timestep | 2 | µs
PSCAD Initialization time | 3.5 | s |  | Atleast 1s
PF flat time | 0.1 | s |  | Atleast 0,1s
PF variable step | TRUE | -
PF enforced sync. | TRUE | -
PF force asymmetrical sim. | FALSE | -
PF enforce P limits in LDF | TRUE | - |  | Can be neccesary to turn off when QDSL is utilized for initialization.
PF enforce Q limits in LDF | TRUE | - |  | Can be neccesary to turn off when QDSL is utilized for initialization.

## Area values
| DK1 |  |  | DK2
Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | Selected
Power-frequency control
LFSM-O start (Hz) | 50.2 | 50.2 | 50.2 | 50.5 | 50.5 | 50.5 | 50.2
LFSM-O droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
LFSM-U start (Hz) | 49.8 | 49.8 | 49.8 | 49.5 | 49.5 | 49.5 | 49.8
LFSM-U droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
FSM deadband (Hz) | 0 | 0 | 0 | 0 | 0 | 0 | 0
FSM droop (%) | 6 | 6 | 6 | 6 | 6 | 6 | 6
FSM provision (%Pn) | 10 | 10 | 10 | 10 | 10 | 10 | 10
30min operation Fmax | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
30min operation Fmin | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Reactive power capability (base Uc)
UQ Q=0pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=0pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=+0.33pu Umax | 1.04 | 1.108 | 1.04 | 1.04 | 1.04 | 1.04 | 1.108
UQ Q=+0.33pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=-0.33pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=-0.33pu Umin | 0.96 | 1.028 | 0.96 | 0.96 | 0.96 | 0.96 | 1.028
Cont. operation Umax | 1.1 | 1.118 | 1.05 | 1.1 | 1.05 | 1.05 | 1.118
Cont. operation Umin | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
60min operation Umax | 1.1 | 1.15 | 1.1 | 1.1 | 1.1 | 1.1 | 1.15
60min operation Umin | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT
LVFT start | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT stop | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
Ures | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
tclear | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Uclear | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec1 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec1 | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec2 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec2 | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
trec3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
OVRT
U1 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3
t1 | 5 | 0.1 | 0.1 | 5 | 0.1 | 0.1 | 0.1
U2 | 1.15 | 1.2 | 1.2 | 1.15 | 1.2 | 1.2 | 1.2
t2 | 60 | 30 | 30 | 60 | 30 | 30 | 30

## RfG cases
|  |  | = Disabled for DSO cases | [8 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1 | TRUE | TRUE | PRE_SS_flatrun_Q1 | 1.0651 | 0 | LFSM | Q | 0 | 10 | 10 | 60 | PF disconnect all ref.
2 | TRUE | TRUE | PRE_SS_flatrun_Q2 | 1.0651 | 0.5 | LFSM | Q | 0.2 | 10 | 10 | 60 | PF disconnect all ref.
3 | TRUE | TRUE | PRE_SS_flatrun_Q3 | 1.0651 | 0.5 | LFSM | Q | -0.2 | 10 | 10 | 60 | PF disconnect all ref.
4 | TRUE | TRUE | PRE_SS_flatrun_Q4 | 1.0651 | 1 | LFSM | Q | 0.33 | 10 | 10 | 60 | PF disconnect all ref.
5 | TRUE | TRUE | PRE_SS_flatrun_Q5 | 1.0651 | 1 | LFSM | Q | -0.33 | 10 | 10 | 60 | PF disconnect all ref.
6 | TRUE | TRUE | PRE_SS_flatrun_Q6 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | PF disconnect all ref.
7 | TRUE | TRUE | PRE_SS_flatrun_Uctrl1 | 0.968 | 0.7 | LFSM | Q(U) | 1.0651 | -1 | 0 | 60 | PF disconnect all ref.
8 | TRUE | TRUE | PRE_SS_flatrun_Uctrl2 | 1.118 | 0.7 | LFSM | Q(U) | 1.0651 | -1 | 0 | 60 | PF disconnect all ref.
9 | TRUE | TRUE | PRE_SS_flatrun_PFctrl1 | 1.0651 | 0.7 | LFSM | PF | 0.949 | 10 | 10 | 60 | PF disconnect all ref.
10 | TRUE | TRUE | PRE_SS_flatrun_PFctrl2 | 1.0651 | 0.7 | LFSM | PF | -0.949 | 10 | 10 | 60 | PF disconnect all ref.
11 | TRUE | TRUE | ION_RfG_P_step_up_0.0_0.5 | 1.0651 | 0 | LFSM | Default | 0 | 10 | 10 | 155 | Pref | 0 | 0.5 | 0
12 | TRUE | TRUE | ION_RfG_P_step_up_0.5_0.7 | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 10 | 80 | Pref | 0 | 0.7 | 0
13 | TRUE | TRUE | ION_RfG_P_step_up_0.7_1.0 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 100 | Pref | 0 | 1 | 0
14 | TRUE | TRUE | ION_RfG_P_step_down_1.0_0.7 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 100 | Pref | 0 | 0.7 | 0
15 | TRUE | TRUE | ION_RfG_P_step_down_0.7_0.5 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 80 | Pref | 0 | 0.5 | 0
16 | TRUE | TRUE | ION_RfG_P_step_down_0.5_0.0 | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 10 | 155 | Pref | 0 | 0 | 0
17 | TRUE | TRUE | ION_RfG_FSM_step1 | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 60 | Frequency | 0 | 50.199 |  | Frequency | 15 | 50 |  | Frequency | 30 | 49.801 |  | Frequency | 45 | 50
18 | TRUE | TRUE | ION_RfG_FSM_step2 | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 60 | Frequency | 0 | 50.15 |  | Frequency | 15 | 50 |  | Frequency | 30 | 49.85 |  | Frequency | 45 | 50
19 | TRUE | TRUE | ION_RfG_LFSM-OU_step1 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
20 | TRUE | TRUE | ION_RfG_LFSM-O_ramp | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 21.5 | Frequency | 0 |  | 0.5 | Frequency | 3 | 51.5 | 0 | Frequency | 5 |  | -0.2 | Frequency | 11.5 | 50.2 | 0
21 | TRUE | TRUE | ION_RfG_LFSM-U_ramp | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 21.5 | Frequency | 0 |  | -0.5 | Frequency | 3 | 48.5 | 0 | Frequency | 5 |  | 0.2 | Frequency | 11.5 | 49.8 | 0
22 | TRUE | TRUE | ION_RfG_FSM_LFSM-O_ramp | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 26.5 | Frequency | 0 |  | 0.2 | Frequency | 7.5 | 51.5 | 0 | Frequency | 9 |  | -0.2 | Frequency | 16.5 | 50 | 0
23 | TRUE | TRUE | ION_RfG_FSM_LFSM-U_ramp | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 26.5 | Frequency | 0 |  | -0.2 | Frequency | 7.5 | 48.5 | 0 | Frequency | 9 |  | 0.2 | Frequency | 16.5 | 50 | 0
24 | TRUE | TRUE | ION_RfG_FSM_LFSM-O_step | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 45 | Frequency | 0 | 50.2 |  | Frequency | 5 | 50.5 |  | Frequency | 10 | 50.2 |  | Frequency | 15 | 50.15 |  | Frequency | 25 | 50.5 |  | Frequency | 35 | 50
25 | TRUE | TRUE | ION_RfG_FSM_LFSM-U_step | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 45 | Frequency | 0 | 49.8 |  | Frequency | 5 | 49.5 |  | Frequency | 10 | 49.8 |  | Frequency | 15 | 49.85 |  | Frequency | 25 | 49.5 |  | Frequency | 35 | 50
26 | TRUE | TRUE | ION_RfG_LFSM-O_Plimited | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 50 | Signal 2 | -1 | 0.5 |  | Frequency | 10 | 51 |  | Frequency | 30 | 50
27 | TRUE | TRUE | ION_RfG_LFSM-U_Plimited | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 10 | 30 | Signal 2 | -1 | 0.8 |  | Frequency | 5 | 48.5 |  | Frequency | 20 | 50
28 | TRUE | TRUE | ION_RfG_U-Q/Pn_Neutral | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 | 100 | Voltage | 0 | 1.118 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 0.968 |  | Voltage | 80 | 1.0651
29 | TRUE | TRUE | ION_RfG_U-Q/Pn_Neutral_stab | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 100 | dVoltage | 0 | 0.052868 |  | dVoltage | 20 | 0 |  | dVoltage | 40 | -0.097132 |  | dVoltage | 80 | 0
30 | TRUE | TRUE | ION_RfG_U-Q/Pn_underEX | 1.0651 | 1 | LFSM | Q | -0.33 | -1 | 0 | 100 | Voltage | 0 | 1.118 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 1.028 |  | Voltage | 80 | 1.0651
31 | TRUE | TRUE | ION_RfG_U-Q/Pn_overEX | 1.0651 | 1 | LFSM | Q | 0.33 | -1 | 0 | 100 | Voltage | 0 | 1.108 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 0.968 |  | Voltage | 80 | 1.0651
32 | TRUE | TRUE | ION_RfG_PQ/Pn_Neutral1 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 155 | Pref | 0 | 0.5
33 | TRUE | TRUE | ION_RfG_PQ/Pn_Neutral2 | 1.0651 | 0.5 | LFSM | Q | 0 | 10 | 10 | 155 | Pref | 0 | 0
34 | TRUE | TRUE | ION_RfG_PQ/Pn_underEX1 | 1.0651 | 1 | LFSM | Q | -0.33 | 10 | 10 | 155 | Pref | 0 | 0.5
35 | TRUE | TRUE | ION_RfG_PQ/Pn_underEX2 | 1.0651 | 0.5 | LFSM | Q | -0.33 | 10 | 10 | 155 | Pref | 0 | 0
36 | TRUE | TRUE | ION_RfG_PQ/Pn_overEX1 | 1.0651 | 1 | LFSM | Q | 0.33 | 10 | 10 | 155 | Pref | 0 | 0.5
37 | TRUE | TRUE | ION_RfG_PQ/Pn_overEX2 | 1.0651 | 0.5 | LFSM | Q | 0.33 | 10 | 10 | 155 | Pref | 0 | 0
38 | TRUE | TRUE | ION_RfG_Ucontrol_Scmin | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 85 | dVoltage | 0 | 0.010651 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.010651 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.021303 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.021303 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
39 | TRUE | TRUE | ION_RfG_Ucontrol_Sctune | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 20 | 15 | 85 | dVoltage | 0 | 0.010651 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.010651 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.021303 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.021303 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
40 | TRUE | TRUE | ION_RfG_Ucontrol_Scmax | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 30 | 20 | 85 | dVoltage | 0 | 0.010651 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.010651 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.021303 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.021303 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
41 | TRUE | TRUE | ION_RfG_Ucontrol_FRTsensitivity | 1 | 1 | LFSM | Q(U) | 1 | -1 | 0 | 75 | Voltage | 2 | 0.85 |  | Voltage | 8 | 0.84 |  | Voltage | 14 | 1 | 0 | Voltage | 30 | 0.84 |  | Voltage | 35 | 1 |  | Voltage | 50 | 0.87 |  | Voltage | 56 | 0.83 |  | Voltage | 62 | 1
42 | TRUE | TRUE | ION_RfG_Ucontrol_FRTsensitivity-ramp | 1 | 1 | LFSM | Q(U) | 1 | -1 | 0 | 20 | Voltage | 2 |  | -0.05 | Voltage | 5.4 | 0.83 | 0 | Voltage | 10.4 |  | 0.1 | Voltage | 12.1 | 1 | 0
43 | TRUE | TRUE | ION_RfG_Uarea_Qreq_1(up) | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 1.118
44 | TRUE | TRUE | ION_RfG_Uarea_Qreq_2(up) | 1.118 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 1.15
45 | TRUE | TRUE | ION_RfG_Uarea_Qreq_1(down) | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.968
46 | TRUE | TRUE | ION_RfG_Uarea_Qreq_2(down) | 0.968 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.9
47 | TRUE | TRUE | ION_RfG_Uarea_Qreq_3(down) | 0.9 | 1 | LFSM | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.85
48 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_1(up) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 1.118
49 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_2(up) | 1.118 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 1.15
50 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_1(down) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 0.968
51 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_2(down) | 0.968 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 0.9
52 | TRUE | TRUE | ION_RfG_Uarea_Q(U)req_3(down) | 0.9 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 | 50 | Voltage | 0 | 0.85
53 | TRUE | TRUE | ION_RfG_Q_control_up | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 120 | Qref | 0 | 0.1 |  | Qref | 30 | 0.2 |  | Qref | 60 | 0.33 |  | Qref | 90 | 0
54 | TRUE | TRUE | ION_RfG_Q_control_down | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 120 | Qref | 0 | -0.1 |  | Qref | 30 | -0.2 |  | Qref | 60 | -0.33 |  | Qref | 90 | 0
55 | TRUE | TRUE | ION_RfG_Qpf_Pfref-change | 1.0651 | 1 | LFSM | PF | 1 | 10 | 10 | 120 | Qref | 0 | 0.95 |  | Qref | 30 | 1 |  | Qref | 60 | -0.95 |  | Qref | 90 | 1
56 | TRUE | TRUE | ION_RfG_Qpf_P-change | 1.0651 | 0.3 | LFSM | PF | 0.99 | 10 | 10 | 135 | Pref | 0 | 0.4 |  | Pref | 35 | 0.5 |  | Pref | 70 | 0.6 |  | Pref | 100 | 0.7
57 | TRUE | TRUE | ION_RfG_SystemGuard | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 45 | Signal 1 | -1 | 1 |  | Signal 3 | 0 | 1 |  | Signal 1 | 0 | 0.5 |  | Signal 1 | 15 | 0.25 |  | Signal 1 | 30 | 1
58 | TRUE | TRUE | ION_RfG_MaxPhaseJump | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 20 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
59 | TRUE | TRUE | ION_RfG_MaxPhaseJump2 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 20 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
60 | TRUE | TRUE | ION_RfG_MaxRoCoF1 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 20 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
61 | TRUE | TRUE | ION_RfG_MaxRoCoF2 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 20 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 | 50 | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
62 | TRUE | TRUE | ION_RfG_MaxRoCoF_CurveOF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 20 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
63 | TRUE | TRUE | ION_RfG_MaxRoCoF_CurveUF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 20 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
64 | TRUE | TRUE | ION_RfG_LVFRT_profile | 1.0651 | 1 | LFSM | Default | 0 | -1 | 0 | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0
65 | TRUE | TRUE | ION_RfG_OVRT_profile | 1.0651 | 1 | LFSM | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 30 | 1.15
66 | TRUE | TRUE | ION_RfG_Fault_3_0 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 0% | 0.15
67 | TRUE | TRUE | ION_RfG_Fault_3_20 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 20% | 0.45
68 | TRUE | TRUE | ION_RfG_Fault_3_40 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 40% | 0.75
69 | TRUE | TRUE | ION_RfG_Fault_3_80 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 80% | 1.35
70 | TRUE | TRUE | ION_RfG_Fault_3_thres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 85% | 1.35
71 | TRUE | TRUE | ION_RfG_Fault_2_0 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 0% | 0.15
72 | TRUE | TRUE | ION_RfG_Fault_2_20 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 20% | 0.45
73 | TRUE | TRUE | ION_RfG_Fault_2_40 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 40% | 0.75
74 | TRUE | TRUE | ION_RfG_Fault_2_80 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 80% | 1.35
75 | TRUE | TRUE | ION_RfG_Fault_2_thres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 85% | 1.35
76 | TRUE | TRUE | ION_RfG_Fault_1_0 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 0% | 0.15
77 | TRUE | TRUE | ION_RfG_Fault_1_20 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 20% | 0.45
78 | TRUE | TRUE | ION_RfG_Fault_1_40 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 40% | 0.75
79 | TRUE | TRUE | ION_RfG_Fault_1_80 | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 80% | 1.35
80 | TRUE | TRUE | ION_RfG_Fault_1_thres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 85% | 1.35
81 | TRUE | TRUE | ION_RfG_Voltage-support | 1.0651 | 1 | LFSM | Default | 0 | -1 | 0 | 5 | Voltage | 0 | 0.7 |  | Voltage | 0.2 | 0.5 |  | Voltage | 0.4 | 0.3 |  | Voltage | 0.6 | 1
82 | TRUE | TRUE | ION_RfG_Fault_1_restrike | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
83 | TRUE | TRUE | ION_RfG_Fault_3_double | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
84 | TRUE | TRUE | ION_RfG_Fault_2_double | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
85 | TRUE | TRUE | ION_RfG_Fault_3_SCR | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 15 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
86 | TRUE | TRUE | ION_RfG_Fault_2_SCR | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 15 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
87 | TRUE | TRUE | EXT_RfG_LFSM-OU_step2 | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 10 | 160 | Frequency | 0 | 50.825 |  | Frequency | 20 | 50 |  | Frequency | 40 | 49.175 |  | Frequency | 60 | 50 |  | Frequency | 80 | 51.45 |  | Frequency | 100 | 50 |  | Frequency | 120 | 48.55 |  | Frequency | 140 | 50
88 | TRUE | TRUE | EXT_RfG_LFSM-OU_step1+FSM | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 | 80 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 50
89 | TRUE | TRUE | EXT_RfG_FSM_rec_pstep | 1.0651 | 0.7 | LFSM+FSM | Default | 0 | 10 | 10 |  | Frequency recording |  | recordings/DK1_frekvens.meas | 1 | Pref | 1 | 0 | 0
90 | TRUE | TRUE | EXT_RfG_LFSMO_ramp+pstep | 1.0651 | 0.5 | LFSM | Default | 0 | 10 | 10 | 40 | Frequency | 0 |  | 0.075 | Frequency | 15 |  | 0 | Pref | 0.1 | 1 |  | Frequency | 20 |  | -0.125 | Frequency | 29 | 50 | 0
91 | TRUE | TRUE | EXT_RfG_LFSM-O_Q_control | 1.0651 | 0.7 | LFSM | Q | 0.1 | 10 | 10 | 40 | Qref | 0 | 0.25 |  | Frequency | 1 | 51 |  | Frequency | 25 | 50 |  | Qref | 27 | 0.1
92 | TRUE | TRUE | EXT_RfG_Ucontrol_LFSM-O | 1.0651 | 0.7 | LFSM | Q(U) | 1.0651 | 10 | 10 | 15 | dVoltage | 0 | -0.1 |  | Frequency | 0.5 |  | 1 | Frequency | 1.5 | 51 | 0 | Frequency | 3.5 |  | -0.5 | Frequency | 5.5 | 50 | 0 | dVoltage | 5 | 0
93 | TRUE | TRUE | EXT_RfG_Ucontrol_Phasejump | 1.0651 | 0.7 | LFSM | Q(U) | 1.0651 | 10 | 10 | 25 | Phase | 0 | 20 |  | dVoltage | 0.02 | -0.075 |  | dVoltage | 15 | 0
94 | TRUE | TRUE | EXT_RfG_Ucontrol_SCR | 1.0651 | 0.7 | LFSM | Q(U) | 1.0651 | 20 | 15 | 25 | SCR | 0 | 10 | 10 | dVoltage | 0.1 | -0.075 |  | dVoltage | 15 | 0
95 | TRUE | TRUE | EXT_RfG_Ucontrol_Fault | 1.0651 | 0.7 | LFSM | Q(U) | 1.0651 | 10 | 10 | 25 | 3p fault | 0 | 20% | 0.45 | dVoltage | 0.451 | -0.075 |  | dVoltage | 15 | 0
96 | TRUE | TRUE | EXT_RfG_Pavail_variation | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 20 | Signal 2 | -1 | 1 |  | Signal 2 | 1 | 0.75 |  | Signal 2 | 5 | 0.25 |  | Signal 2 | 10 | 1
97 | TRUE | TRUE | EXT_RfG_MaxPhaseJump_Extreme | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 20 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | -40 |  | Phase | 7.5 | 0
98 | TRUE | TRUE | EXT_RfG_RoCoF_ACER-CurveOF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 12 | Frequency | 0 |  | 4 | Frequency | 0.25 |  | 1.3333 | Frequency | 1 |  | 0.33333 | Frequency | 2.5 |  | 0 | Frequency | 4.5 |  | -1 | Frequency | 5.5 |  | 0
99 | TRUE | TRUE | EXT_RfG_RoCoF_ACER-CurveUF | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 12 | Frequency | 0 |  | -4 | Frequency | 0.25 |  | -1.33 | Frequency | 1 |  | -0.333 | Frequency | 2.5 |  | 0 | Frequency | 4.5 |  | 1 | Frequency | 6 |  | 0
100 | TRUE | TRUE | EXT_RfG_RoCoF+PhaseJump1 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 12 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | -20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
101 | TRUE | TRUE | EXT_RfG_RoCoF+PhaseJump2 | 1.0651 | 0.7 | LFSM | Default | 0 | 10 | 10 | 12 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | 20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
102 | TRUE | TRUE | EXT_RfG_Fault_3_0_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 3p fault | 0 | 0% | 0.15
103 | TRUE | TRUE | EXT_RfG_Fault_3_20_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 3p fault | 0 | 20% | 0.45
104 | TRUE | TRUE | EXT_RfG_Fault_3_40_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 3p fault | 0 | 40% | 0.75
105 | TRUE | TRUE | EXT_RfG_Fault_3_80_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 3p fault | 0 | 80% | 1.35
106 | TRUE | TRUE | EXT_RfG_Fault_3_thres_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 3p fault | 0 | 85% | 1.35
107 | TRUE | TRUE | EXT_RfG_Fault_2_20_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 2p-g fault | 0 | 20% | 0.45
108 | TRUE | TRUE | EXT_RfG_Fault_2_40_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 2p-g fault | 0 | 40% | 0.75
109 | TRUE | TRUE | EXT_RfG_Fault_2_80_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 2p-g fault | 0 | 80% | 1.35
110 | TRUE | TRUE | EXT_RfG_Fault_1_20_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 1p fault | 0 | 20% | 0.45
111 | TRUE | TRUE | EXT_RfG_Fault_1_40_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 1p fault | 0 | 40% | 0.75
112 | TRUE | TRUE | EXT_RfG_Fault_1_80_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 1p fault | 0 | 80% | 1.35
113 | TRUE | TRUE | EXT_RfG_Fault_3_SCR_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 20 | 15 | 15 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
114 | TRUE | TRUE | EXT_RfG_Fault_2_SCR_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 20 | 15 | 15 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
115 | TRUE | TRUE | EXT_RfG_Fault_3_UnderThres_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 12 | 3p fault | 0 | 83% | 1.35
116 | TRUE | TRUE | EXT_RfG_Fault_3_UnderThres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 83% | 1.35
117 | TRUE | TRUE | EXT_RfG_Fault_1_UnderThres | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 83% | 1.35
118 | TRUE | TRUE | EXT_RfG_Fault_2_double_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
119 | TRUE | TRUE | EXT_RfG_Fault_double-mix_SCR | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 15 | 2p fault | 0 | 30% | 0.15 | 3p fault | 1.65 | 30% | 0.15 | SCR | 1.799 | 10 | 10
120 | TRUE | TRUE | EXT_RfG_Fault_3_20_WG | 1.0651 | 1 | LFSM | Default | 0 | 2 | 3 | 20 | 3p fault | 0 | 20% | 0.2
121 | TRUE | TRUE | EXT_RfG_Fault_2_20_WG | 1.0651 | 1 | LFSM | Default | 0 | 2 | 3 | 20 | 2p-g fault | 0 | 20% | 0.2
122 | TRUE | TRUE | EXT_RfG_Fault_3_ROCOF_curveOF | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 15 | 3p fault | 0 | 40% | 0.2 | Frequency | 1.21 |  | 4 | Frequency | 1.26 |  | 2 | Frequency | 1.36 |  | 1 | Frequency | 2.11 |  | 0.35 | Frequency | 3.11 |  | 0 | Frequency | 5.11 |  | -1 | Frequency | 6.11 |  | 0
123 | TRUE | TRUE | EXT_RfG_Fault_3_ROCOF_curveUF | 1.0651 | 1 | LFSM | Default | 0 | 10 | 10 | 15 | 3p fault | 0 | 40% | 0.2 | Frequency | 1.21 |  | -4 | Frequency | 1.26 |  | -2 | Frequency | 1.36 |  | -1 | Frequency | 2.11 |  | -0.35 | Frequency | 3.11 |  | 0 | Frequency | 5.11 |  | 1 | Frequency | 6.11 |  | 0
124 | TRUE | TRUE | EXT_RfG_Fault_3_SCR_freqStep1 | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 20 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 6 | 50
125 | TRUE | TRUE | EXT_RfG_Fault_3_SCR_freqStep2 | 1.0651 | 1 | LFSM | Default | 0 | 20 | 15 | 20 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 4 | 50
126 | TRUE | TRUE | EXT_SCR_step_Max-Min | 1.0651 | 1 | LFSM | Default | 0 | 30 | 20 | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
127 | TRUE | TRUE | EXT_SCR_step_Max-Min_NotDef | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 30 | 20 | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
128 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
129 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q(U) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
130 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q_SCmin | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
131 | TRUE | TRUE | EXT_RfG_Fault_rec_1_Q(U)_SCmin | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | 10 | 10 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
132 | TRUE | TRUE | EXT_RfG_Fault_rec_2_Q | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault2.meas | 1.0651
133 | TRUE | TRUE | EXT_RfG_Fault_rec_2_Q(U) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault2.meas | 1.0651
134 | TRUE | TRUE | EXT_RfG_Fault_rec_3_Q | 1.0651 | 1 | LFSM | Q | 0 | -1 | 0 |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
135 | TRUE | TRUE | EXT_RfG_Fault_rec_3_Q(U) | 1.0651 | 1 | LFSM | Q(U) | 1.0651 | -1 | 0 |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
136 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.2 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.2 | 0
137 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.3 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.3 | 0
138 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.4 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.4 | 0
139 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_1.5 | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.5 | 0
140 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_insta_min | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 7 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
141 | TRUE | TRUE | EXT_RfG_proc_VoltageRise_insta_max | 1.0651 | 1 | LFSM | Q | 0 | 30 | 20 | 7 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
142 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.8pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | 3p fault | 0 | 80% | 60
143 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.6pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | 3p fault | 0 | 60% | 60
144 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.40pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | 3p fault | 0 | 40% | 60
145 | TRUE | TRUE | EXT_RfG_proc_Fault_3_0.20pu | 1.0651 | 1 | LFSM | Q | 0 | 10 | 10 | 60 | 3p fault | 0 | 20% | 60
146 | TRUE | TRUE | EXT_RfG_proc_Freq_51.6Hz | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 10 | 60 | Frequency | 0 | 51.6
147 | TRUE | TRUE | EXT_RfG_proc_Freq_47.4Hz | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 10 | 60 | Frequency | 0 | 47.4
148 | TRUE | TRUE | EXT_RfG_proc_Freq_limit_up | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 10 | 40 | Frequency | 0 | 52 |  | Frequency | 8 | 53 |  | Frequency | 16 | 54 |  | Frequency | 24 | 55 |  | Frequency | 32 | 56 |  | Frequency | 35 | 50
149 | TRUE | TRUE | EXT_RfG_proc_Freq_limi_down | 1.0651 | 0.7 | LFSM | Q | 0 | 10 | 10 | 40 | Frequency | 0 | 47 |  | Frequency | 8 | 46 |  | Frequency | 16 | 45 |  | Frequency | 24 | 44 |  | Frequency | 32 | 43 |  | Frequency | 35 | 50
150 | TRUE | TRUE | EXT_RfG_proc_Fault_1_0.05pu | 1.0651 | 1 | LFSM | Q | 0 | 30 | 10 | 60 | 1p fault | 0 | 5% | 60

## DCC cases
|  |  | DSO plants only RfG cases and deactive coloured. | [8 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1001 | TRUE | TRUE | DCC_Fault_3_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 0% | 0.15
1002 | TRUE | TRUE | DCC_Fault_3_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 20% | 0.45
1003 | TRUE | TRUE | DCC_Fault_3_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 40% | 0.75
1004 | TRUE | TRUE | DCC_Fault_3_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 80% | 1.35
1005 | TRUE | TRUE | DCC_Fault_2_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 0% | 0.15
1006 | TRUE | TRUE | DCC_Fault_2_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 20% | 0.45
1007 | TRUE | TRUE | DCC_Fault_2_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 40% | 0.75
1008 | TRUE | TRUE | DCC_Fault_2_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 80% | 1.35
1009 | TRUE | TRUE | DCC_Fault_1_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 0% | 0.15
1010 | TRUE | TRUE | DCC_Fault_1_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 20% | 0.45
1011 | TRUE | TRUE | DCC_Fault_1_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 40% | 0.75
1012 | TRUE | TRUE | DCC_Fault_1_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 80% | 1.35
1013 | TRUE | TRUE | DCC_Fault_3_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
1014 | TRUE | TRUE | DCC_Fault_2_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
1015 | TRUE | TRUE | DCC_SCR_step_Max-Min | 1.0651 | 1 | No P(f) | Default | 0 | 30 | 20 | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
1016 | TRUE | TRUE | DCC_HVRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 30 | Voltage | 0 | 1.15 | 0 | Voltage | 10 | 1.2 | 0 | Voltage | 17 | 1.3 | 0 | Voltage | 25 | 1
1017 | TRUE | TRUE | DCC_UVRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 45 | Voltage | 0 | 0.9 |  | Voltage | 10 | 0.85 |  | Voltage | 17 | 0.8 |  | Voltage | 25 | 0.7 |  | Voltage | 32 | 0.6 |  | Voltage | 37 | 1
1018 | TRUE | TRUE | DCC_SystemGuard | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 45 | Signal 1 | -1 | 1 |  | Signal 1 | 0 | 0.5 |  | Signal 1 | 15 | 0.25 |  | Signal 1 | 30 | 1
1019 | TRUE | TRUE | DCC_MaxPhaseJump | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
1020 | TRUE | TRUE | DCC_MaxPhaseJump2 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
1021 | TRUE | TRUE | DCC_MaxRoCoF1 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
1022 | TRUE | TRUE | DCC_MaxRoCoF2 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 5 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 | 50 | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
1023 | TRUE | TRUE | DCC_MaxRoCoF_CurveOF | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
1024 | TRUE | TRUE | DCC_MaxRoCoF_CurveUF | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
1025 | TRUE | TRUE | DCC_LFSM-OU_step1 | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
1026 | TRUE | TRUE | DCC_LFSM-O_ramp | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 21.5 | Frequency | 0 |  | 0.5 | Frequency | 3 | 51.5 | 0 | Frequency | 5 |  | -0.2 | Frequency | 11.5 | 50.2 | 0
1027 | TRUE | TRUE | DCC_LFSM-U_ramp | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 21.5 | Frequency | 0 |  | -0.5 | Frequency | 3 | 48.5 | 0 | Frequency | 5 |  | 0.2 | Frequency | 11.5 | 49.8 | 0
1028 | TRUE | TRUE | DCC_LFDD | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | Frequency | 0 | 48.9 |  | Frequency | 10 | 48.8 |  | Frequency | 20 | 48.6 |  | Frequency | 30 | 48.4 |  | Frequency | 40 | 48.2 |  | Frequency | 50 | 50
1029 | TRUE | TRUE | DCC_Faera-O | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | Frequency | 0 | 50.5 |  | Frequency | 10 | 51 |  | Frequency | 20 | 51.5 |  | Frequency | 30 | 52 |  | Frequency | 40 | 53 |  | Frequency | 50 | 50
1030 | TRUE | TRUE | DCC_Faera-U | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 70 | Frequency | 0 | 49.5 |  | Frequency | 10 | 49 |  | Frequency | 20 | 48 |  | Frequency | 30 | 47.5 |  | Frequency | 40 | 47 |  | Frequency | 50 | 46.5 |  | Frequency | 60 | 50
1031 | TRUE | TRUE | DCC_Uarea_Qreq_1(up) | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.118
1032 | TRUE | TRUE | DCC_Uarea_Qreq_2(up) | 1.118 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.15
1033 | TRUE | TRUE | DCC_Uarea_Qreq_1(down) | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 0.968
1034 | TRUE | TRUE | DCC_Uarea_Qreq_2(down) | 0.968 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 0.9
1035 | TRUE | TRUE | DCC_Uarea_Qreq_3(down) | 0.9 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 0.85
1036 | TRUE | TRUE | DCC_VoltageRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.05 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.05 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.05 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.05 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.05 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.05 | 1
1037 | TRUE | TRUE | DCC_VoltageDip_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Voltage | 0 | 0.9 | 0 | Voltage | 0.05 | 1 |  | Voltage | 1 | 0.85 |  | Voltage | 1.05 | 1 |  | Voltage | 2 | 0.8 |  | Voltage | 2.05 | 1 |  | Voltage | 3 | 0.75 |  | Voltage | 3.05 | 1 |  | Voltage | 4 | 0.7 |  | Voltage | 4.05 | 1 |  | Voltage | 5 | 0.65 |  | Voltage | 5.05 | 1
1038 | TRUE | TRUE | DCC_freqRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 | 52 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 52.5 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 53 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 55 |  | Frequency | 3.05 | 50 |  | Frequency | 4 | 60 |  | Frequency | 4.05 | 50 |  | Frequency | 5 | 65 |  | Frequency | 5.05 | 50
1039 | TRUE | TRUE | DCC_freqDip_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 | 47.5 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 47 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 46.5 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 46 |  | Frequency | 3.05 | 50

## Unit cases
[12 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
2001 | TRUE | TRUE | UNT_SS_flatrun_Q1 | 1.0651 | 0 | No P(f) | Default | 0 | 10 | 10 | 60 | PF disconnect all ref.
2002 | TRUE | TRUE | UNT_SS_flatrun_Q2 | 1.0651 | 0.5 | No P(f) | Default | 0.2 | 10 | 10 | 60 | PF disconnect all ref.
2003 | TRUE | TRUE | UNT_SS_flatrun_Q3 | 1.0651 | 0.5 | No P(f) | Default | -0.2 | 10 | 10 | 60 | PF disconnect all ref.
2004 | TRUE | TRUE | UNT_SS_flatrun_Q4 | 1.0651 | 1 | No P(f) | Default | 0.33 | 10 | 10 | 60 | PF disconnect all ref.
2005 | TRUE | TRUE | UNT_SS_flatrun_Q5 | 1.0651 | 1 | No P(f) | Default | -0.33 | 10 | 10 | 60 | PF disconnect all ref.
2006 | TRUE | TRUE | UNT_SS_flatrun_Q6 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | PF disconnect all ref.
2007 | TRUE | TRUE | UNT_P_step_up_0.5_0.7 | 1.0651 | 0.5 | No P(f) | Default | 0 | 10 | 10 | 20 | Pref | 0 | 0.7 | 0 | Pref | 10 | 0.5
2008 | TRUE | TRUE | UNT_Q_control_up | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 20 | Qref | 0 | 0.1 |  | Qref | 5 | 0.2 |  | Qref | 10 | -0.1 |  | Qref | 15 | 0
2009 | TRUE | TRUE | UNT_U-Q/Pn_Neutral | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 20 | Voltage | 0 | 1.118 |  | Voltage | 5 | 1.0651 |  | Voltage | 10 | 0.968 |  | Voltage | 15 | 1.0651
2010 | TRUE | TRUE | UNT_fArea | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
2011 | TRUE | TRUE | UNT_LVFRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0
2012 | TRUE | TRUE | UNT_OVRT_profile | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 50 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 30 | 1.15
2013 | TRUE | TRUE | UNT_Fault_3_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 0% | 0.15
2014 | TRUE | TRUE | UNT_Fault_3_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 20% | 0.45
2015 | TRUE | TRUE | UNT_Fault_3_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 40% | 0.75
2016 | TRUE | TRUE | UNT_Fault_3_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 3p fault | 0 | 80% | 1.35
2017 | TRUE | TRUE | UNT_Fault_2_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 0% | 0.15
2018 | TRUE | TRUE | UNT_Fault_2_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 20% | 0.45
2019 | TRUE | TRUE | UNT_Fault_2_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 40% | 0.75
2020 | TRUE | TRUE | UNT_Fault_2_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 2p-g fault | 0 | 80% | 1.35
2021 | TRUE | TRUE | UNT_Fault_1_0 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 0% | 0.15
2022 | TRUE | TRUE | UNT_Fault_1_20 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 20% | 0.45
2023 | TRUE | TRUE | UNT_Fault_1_40 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 40% | 0.75
2024 | TRUE | TRUE | UNT_Fault_1_80 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 12 | 1p fault | 0 | 80% | 1.35
2025 | TRUE | TRUE | UNT_Voltage-support | 1.0651 | 1 | No P(f) | Default | 0 | -1 | 0 | 5 | Voltage | 0 | 70% |  | Voltage | 0.2 | 0.5 |  | Voltage | 0.4 | 0.3 |  | Voltage | 0.6 | 1
2026 | TRUE | TRUE | UNT_Fault_1_restrike | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
2027 | TRUE | TRUE | UNT_Fault_3_double | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
2028 | TRUE | TRUE | UNT_Fault_2_double | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
2029 | TRUE | TRUE | UNT_Fault_3_20_short | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 2 | 3p fault | 0 | 20% | 0.25 | SCR | 0.249 | 10 | 10
2030 | TRUE | TRUE | UNT_Fault_2_20_short | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 2 | 2p-g fault | 0 | 20% | 0.25
2031 | TRUE | TRUE | UNT_Fault_3_20_WG | 1.0651 | 1 | No P(f) | Default | 0 | 2 | 3 | 12 | 3p fault | 0 | 20% | 0.2
2032 | TRUE | TRUE | UNT_Fault_2_20_WG | 1.0651 | 1 | No P(f) | Default | 0 | 2 | 3 | 12 | 2p-g fault | 0 | 20% | 0.2
2033 | TRUE | TRUE | UNT_Fault_3_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
2034 | TRUE | TRUE | UNT_Fault_2_SCR | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
2035 | TRUE | TRUE | UNT_Fault_3_SCR_freqStep | 1.0651 | 1 | No P(f) | Default | 0 | 20 | 15 | 12 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 5.5 | 50
2036 | TRUE | TRUE | Unit_SCR_step_Max-Min | 1.0651 | 1 | No P(f) | Default | 0 | 30 | 20 | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
2037 | TRUE | TRUE | UNT_MaxPhaseJump | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
2038 | TRUE | TRUE | UNT_MaxPhaseJump2 | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
2039 | TRUE | TRUE | UNT_MaxRoCoF_CurveOF | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
2040 | TRUE | TRUE | UNT_MaxRoCoF_CurveUF | 1.0651 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
2041 | TRUE | TRUE | UNT_MaxPhaseJump_Extreme_min | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
2042 | TRUE | TRUE | UNT_MaxPhaseJump_Extreme_max | 1.0651 | 1 | No P(f) | Default | 0 | 30 | 20 | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
2043 | TRUE | TRUE | UNT_VoltageRise_1.2 | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.2 | 0
2044 | TRUE | TRUE | UNT_VoltageRise_1.3 | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.3 | 0
2045 | TRUE | TRUE | UNT_VoltageRise_1.4 | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.4 | 0
2046 | TRUE | TRUE | UNT_VoltageRise_1.5 | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | dVoltage | 0 | 0.5 | 0
2047 | TRUE | TRUE | UNT_VoltageRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
2048 | TRUE | TRUE | UNT_VoltageRise_insta_max | 1 | 1 | No P(f) | Default | 0 | 30 | 20 | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
2049 | TRUE | TRUE | Unit_freqRise_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 | 52 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 52.5 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 53 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 55 |  | Frequency | 3.05 | 50 |  | Frequency | 4 | 60 |  | Frequency | 4.05 | 50 |  | Frequency | 5 | 65 |  | Frequency | 5.05 | 50
2050 | TRUE | TRUE | Unit_freqDip_insta_min | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 10 | Frequency | 0 | 47.5 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 47 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 46.5 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 46 |  | Frequency | 3.05 | 50
2051 | TRUE | TRUE | UNT_prot_Fault_3_0.8pu | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | 3p fault | 0 | 80% | 60
2052 | TRUE | TRUE | UNT_prot_Fault_3_0.6pu | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | 3p fault | 0 | 60% | 60
2053 | TRUE | TRUE | UNT_prot_Fault_3_0.40pu | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | 3p fault | 0 | 40% | 60
2054 | TRUE | TRUE | UNT_prot_Fault_3_0.20pu | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | 3p fault | 0 | 20% | 60
2055 | TRUE | TRUE | UNT_prot_Fault_1_0.05pu | 1 | 1 | No P(f) | Default | 0 | 10 | 10 | 60 | 1p fault | 0 | 5% | 60
2056 | TRUE | TRUE | UNT_Freq_53Hz | 1 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 60 | Frequency | 0 | 53
2057 | TRUE | TRUE | UNT_Freq_46Hz | 1 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 60 | Frequency | 0 | 46
2058 | TRUE | TRUE | UNT_Freq_limit_up | 1 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 30 | Frequency | 0 | 52 |  | Frequency | 5 | 53 |  | Frequency | 10 | 54 |  | Frequency | 15 | 55 |  | Frequency | 20 | 56 |  | Frequency | 25 | 50
2059 | TRUE | TRUE | UNT_Freq_limi_down | 1 | 0.7 | No P(f) | Default | 0 | 10 | 10 | 30 | Frequency | 0 | 47 |  | Frequency | 5 | 46 |  | Frequency | 10 | 45 |  | Frequency | 15 | 44 |  | Frequency | 20 | 43 |  | Frequency | 25 | 50
2060 | FALSE | TRUE | UNT_Pavail_variation | 1.0651 | 1 | No P(f) | Default | 0 | 10 | 10 | 20 | Signal 2 | 1 | 0.75 |  | Signal 2 | 5 | 0.25 |  | Signal 2 | 10 | 1

## Custom cases
[12 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
3001 | TRUE | FALSE | Custom_1 | 1.0651 | 1 | No P(f) | Qmode3 | 0 | 30 | 20 | 5 | 3p fault | 0.1 | 5% | 0.1 | Qref | 1 | 0.1

## Event types
Name | Description | X1 description | X1 unit | X2 description | X2 unit
Pref | Pref change | setpoint, base Pn | pu | gradient | 1/s
Qref | Qref change | setpoint, base Pn | pu | gradient | 1/s
Voltage | Grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
dVoltage | Delta grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
Phase | Grid phase change (thevenin) | setpoint | degree | gradient | degree/s
Frequency | Grid frequency change | setpoint | Hz | gradient | Hz/s
SCR | Grid impedance change | SCR | - | X/R | -
3p fault | Three phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p-g fault | Two phase to ground fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p fault | Two phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
1p fault | One phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
3p fault (ohm) | Three phase fault | fault resistance | ohm | fault reactance | ohm
2p-g fault (ohm) | Two phase to ground fault | fault resistance | ohm | fault reactance | ohm
2p fault (ohm) | Two phase fault | fault resistance | ohm | fault reactance | ohm
1p fault (ohm) | One phase fault | fault resistance | ohm | fault reactance | ohm
Clear fault | Clear any fault | N/A | N/A | N/A | N/A
Pref recording | Use external measurement file for Pref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Qref recording | Use external measurement file for Qref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Voltage recording | Use external measurement file for the thevenin voltage signal (RMS). First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Inst. Voltage recording | Only supported for PSCAD. Use external measurement file for the thevenin instantaneous voltages. Time value ignored. | Relative path to measurementfile | N/A | Scaling factor | -
Phase recording | Use external measurement file for the thevenin voltage phase signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Frequency recording | Use external measurement file for the thevenin voltage frequency signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 1 | Custom signal 1 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 2 | Custom signal 2 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 3 | Custom signal 3 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 4 | Custom signal 4 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 5 | Custom signal 5 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 6 | Custom signal 6 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 7 | Custom signal 7 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 8 | Custom signal 8 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 9 | Custom signal 9 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 10 | Custom signal 10 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 1 recording | Use external measurement file for custom signal 1. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 2 recording | Use external measurement file for custom signal 2. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 3 recording | Use external measurement file for custom signal 3. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 4 recording | Use external measurement file for custom signal 4. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 5 recording | Use external measurement file for custom signal 5. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 6 recording | Use external measurement file for custom signal 6. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 7 recording | Use external measurement file for custom signal 7. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 8 recording | Use external measurement file for custom signal 8. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 9 recording | Use external measurement file for custom signal 9. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 10 recording | Use external measurement file for custom signal 10. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
PF disconnect all ref. | In Powerfactory out-of-service all references (including custom signals) to plant. For initialization testing purposes. | N/A | N/A | N/A | N/A
PF force asymmetrical | Force case to be simulated asymmetricaly. | N/A | N/A | N/A | N/A

## RfG cases overview
Rank | Name | Category | Comment
1 | PRE_SS_flatrun_Q1 | Steady state - model performance/convergence | PRE-run cases to check model is correctly setup with MTB and can properly flatrun.
2 | PRE_SS_flatrun_Q2 |  | Test of model performance, flatrun in several operation points and Q-modes
3 | PRE_SS_flatrun_Q3 |  | -
4 | PRE_SS_flatrun_Q4 |  | -
5 | PRE_SS_flatrun_Q5 |  | -
6 | PRE_SS_flatrun_Q6 |  | -
7 | PRE_SS_flatrun_Uctrl1 |  | -
8 | PRE_SS_flatrun_Uctrl2 |  | -
9 | PRE_SS_flatrun_PFctrl1 |  | -
10 | PRE_SS_flatrun_PFctrl2 |  | -
11 | ION_RfG_P_step_up_0.0_0.5 | Active power | Test of active power ramping. Check compliance with max ramp rate 20%Pn/min
12 | ION_RfG_P_step_up_0.5_0.7 |  | Test model function in various operation points.
13 | ION_RfG_P_step_up_0.7_1.0 |  | -
14 | ION_RfG_P_step_down_1.0_0.7 |  | -
15 | ION_RfG_P_step_down_0.7_0.5 |  | -
16 | ION_RfG_P_step_down_0.5_0.0 |  | -
17 | ION_RfG_FSM_step1 | Frequency | Test of FSM (full frequency range)
18 | ION_RfG_FSM_step2 |  | Test FSM follows droop correctly, case should ensure half power change of FSM limit (+/-5% power) (not working yet)
19 | ION_RfG_LFSM-OU_step1 |  | Test of LFSM (full range)
20 | ION_RfG_LFSM-O_ramp |  | Test of LFSM-O with ramp
21 | ION_RfG_LFSM-U_ramp |  | Test of LFSM-U with ramp
22 | ION_RfG_FSM_LFSM-O_ramp |  | Test of transition between FSM and LFSM during ramping.
23 | ION_RfG_FSM_LFSM-U_ramp |  | -
24 | ION_RfG_FSM_LFSM-O_step |  | Test of transition between FSM and LFSM during steps
25 | ION_RfG_FSM_LFSM-U_step |  | -
26 | ION_RfG_LFSM-O_Plimited |  | Test of LFSM-O with limited available power. PPC setpoint does not match the actual power production, so can it handle this ?
27 | ION_RfG_LFSM-U_Plimited |  | Test of LFSM-U with limited available power. PPC setpoint does not match the actual power production, so can it handle this ?
28 | ION_RfG_U-Q/Pn_Neutral | Reactive power capability + voltage control | Test of reactive power capability. (fixed Q setpoint and varying voltage), Q = 0
29 | ION_RfG_U-Q/Pn_Neutral_stab |  | Test of stability when fixed Q setpoint and varying voltage, Q = 0
30 | ION_RfG_U-Q/Pn_underEX |  | Test of reactive power capability. (fixed Q setpoint and varying voltage), Q = -0.33pu
31 | ION_RfG_U-Q/Pn_overEX |  | Test of reactive power capability. (fixed Q setpoint and varying voltage), Q = 0.33pu
32 | ION_RfG_PQ/Pn_Neutral1 |  | Test of reactive power capability when changing P setpoint, Q = 0. Important: For large plants and low SCR it may not be realistic to change power from 1pu-0 without changing the POC voltage too much. When relevant split the simulation into multiple with different starting points.
33 | ION_RfG_PQ/Pn_Neutral2 |  | Test of reactive power capability when changing P setpoint, Q = 0
34 | ION_RfG_PQ/Pn_underEX1 |  | Test of reactive power capability when changing P setpoint, Q = -0.33pu
35 | ION_RfG_PQ/Pn_underEX2 |  | Test of reactive power capability when changing P setpoint, Q = -0.33pu
36 | ION_RfG_PQ/Pn_overEX1 |  | Test of reactive power capability when changing P setpoint, Q = 0.33pu
37 | ION_RfG_PQ/Pn_overEX2 |  | Test of reactive power capability when changing P setpoint, Q = 0.33pu
38 | ION_RfG_Ucontrol_Scmin |  | Test of reactive power capability and voltage control performance (minimum SC)
39 | ION_RfG_Ucontrol_Sctune |  | Test of reactive power capability and voltage control performance ("medium" SC)
40 | ION_RfG_Ucontrol_Scmax |  | Test of reactive power capability and voltage control performance (max SC)
41 | ION_RfG_Ucontrol_FRTsensitivity |  | Test how voltage control performs just around FRT threshold. (Focus is plant performance, plant should not suddenly reduce the reactive current when going from "low" voltage and into FRT). Important: This simulation is not realistic scenario and should not be used for GC compliance, but is a screening of stability risk/voltage control performance. It is not a requirement that plants can handle 3 consecutive voltage drops in this manner. When relevant simulation should be split into multiple cases and modified in order to make scenarious representative of real operation and do further assessment of any stability risk
42 | ION_RfG_Ucontrol_FRTsensitivity-ramp |  | Test how voltage control performs just around FRT threshold. (Focus is plant performance, plant should not suddenly reduce the reactive current when going from "low" voltage and into FRT). Now with ramping voltage transition from above to below FRT limit
43 | ION_RfG_Uarea_Qreq_1(up) | Reactive power in full voltage range | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (fixed Q setpoint)
44 | ION_RfG_Uarea_Qreq_2(up) |  | -
45 | ION_RfG_Uarea_Qreq_1(down) |  | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (fixed Q setpoint)
46 | ION_RfG_Uarea_Qreq_2(down) |  | Note: Depending on system, steps 2 and 3 may be the same as step 1. Step 1 goes to limits of UQ, step 2 goes to continues voltage limit, step 3 goes to time restricted voltage limit (FRT limit)
47 | ION_RfG_Uarea_Qreq_3(down) |  | -
48 | ION_RfG_Uarea_Q(U)req_1(up) |  | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (U-control)
49 | ION_RfG_Uarea_Q(U)req_2(up) |  | -
50 | ION_RfG_Uarea_Q(U)req_1(down) |  | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (U-control)
51 | ION_RfG_Uarea_Q(U)req_2(down) |  | Note: Depending on system, steps 2 and 3 may be the same as step 1. Step 1 goes to limits of UQ, step 2 goes to continues voltage limit, step 3 goes to time restricted voltage limit (FRT limit)
52 | ION_RfG_Uarea_Q(U)req_3(down) |  | -
53 | ION_RfG_Q_control_up | Q-mode and Pf-mode regulation | Test performance in Q-control, when changing setpoint. Important: Plant should be allowed time to optimize tap changers between each Q step and depending on SCR, Q steps should not be so large the POC voltage is changed drastically. When relevant extend the time period of each step or split the simulation into multiple with different starting points.
54 | ION_RfG_Q_control_down |  | Test performance in Q-control, when changing setpoint. Important: same as above
55 | ION_RfG_Qpf_Pfref-change |  | Test performance in Pf-control, when changing power factor setpoint. Important: same as above
56 | ION_RfG_Qpf_P-change |  | Test performance in Pf-control, when changing P setpoint. Important: same as above
57 | ION_RfG_SystemGuard | Systemguard | Test model includes SIPS function and performance is compliant
58 | ION_RfG_MaxPhaseJump | Plant robustness | Test plant is compliant with 20deg phase jumps (large jumps)
59 | ION_RfG_MaxPhaseJump2 |  | Test of phasejump robustness with several consecutive smaller phasejumps adding up to 20deg over 3 periods
60 | ION_RfG_MaxRoCoF1 |  | Test of robusstness for RoCoF (RoCoF of either 2Hz/s or 0.5Hz/s for long time)
61 | ION_RfG_MaxRoCoF2 |  | Test of robusstness for RoCoF (RoCoF of either 4Hz/s for just 100ms or 20Hz/s for 20ms.)
62 | ION_RfG_MaxRoCoF_CurveOF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - over frequency
63 | ION_RfG_MaxRoCoF_CurveUF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - under frequency
64 | ION_RfG_LVFRT_profile |  | Test of LVRT robustness (standard profile)
65 | ION_RfG_OVRT_profile |  | Test of HVRT robustness (standard profile)
66 | ION_RfG_Fault_3_0 | Faults | Fault simulations test of robustness/stability and compliance with PFAPR + reactive fault current
67 | ION_RfG_Fault_3_20 |  | -
68 | ION_RfG_Fault_3_40 |  | -
69 | ION_RfG_Fault_3_80 |  | -
70 | ION_RfG_Fault_3_thres |  | Screening what happens just around FRT threshold - any toggling ?
71 | ION_RfG_Fault_2_0 |  | -
72 | ION_RfG_Fault_2_20 |  | -
73 | ION_RfG_Fault_2_40 |  | -
74 | ION_RfG_Fault_2_80 |  | -
75 | ION_RfG_Fault_2_thres |  | Screening what happens just around FRT threshold - any toggling ?
76 | ION_RfG_Fault_1_0 |  | -
77 | ION_RfG_Fault_1_20 |  | -
78 | ION_RfG_Fault_1_40 |  | -
79 | ION_RfG_Fault_1_80 |  | -
80 | ION_RfG_Fault_1_thres |  | Screening what happens just around FRT threshold - any toggling ?
81 | ION_RfG_Voltage-support |  | Test of reactive fault current contribution, match required static
82 | ION_RfG_Fault_1_restrike |  | Test of robustness for consecutive faults - single fase with auto reclosure. 2 different faults each with double strike.
83 | ION_RfG_Fault_3_double |  | Test of robustness for consecutive faults - 3 phase fault, 2 individual faults in a row
84 | ION_RfG_Fault_2_double |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row
85 | ION_RfG_Fault_3_SCR |  | Test of stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
86 | ION_RfG_Fault_2_SCR |  | Test of stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
87 | EXT_RfG_LFSM-OU_step2 | Extra Frequency tests | Test of LFSM follows correct droop. Designed to ensure first steps result in +/- 25% power change, then +/- 50% power change
88 | EXT_RfG_LFSM-OU_step1+FSM |  | The original (ION) step test of LFSM, now with FSM active
89 | EXT_RfG_FSM_rec_pstep |  | Test with playback of real frequency measurement. Test of FSM based on f-measurement while changing active power setpoint. Constant and minor variations in frequency barely activating FSM while changing active power reference. Mainly test that model performance/convergence can handle real signal with constant variation. Potentially also indicator of real plant challenges.
90 | EXT_RfG_LFSMO_ramp+pstep |  | Test of LFSM-O activation during setpoint change (when active power varies). When exit LFSM plant should return to same Power as was at LFSM activation and then continue ramp from there.
91 | EXT_RfG_LFSM-O_Q_control | Extra testing reactive power/voltage control | Test of LFSM-O activation during Q setpoint change. (mostly about model robustness/performance; can model regulate active and reactive power at the same time. Not so much compliance)
92 | EXT_RfG_Ucontrol_LFSM-O |  | Test of simultanious voltage control and frequency control. (mostly about model robustness/performance; can model regulate active and reactive power at the same time. Not so much compliance)
93 | EXT_RfG_Ucontrol_Phasejump |  | Test of Ucontrol, voltage change and phasejump. (Plant performance / compliance)
94 | EXT_RfG_Ucontrol_SCR |  | Test of Ucontrol, voltage change and impedans change. (Plant performance / compliance)
95 | EXT_RfG_Ucontrol_Fault |  | Test of Ucontrol, voltage change and fault. (Plant performance / compliance)
96 | EXT_RfG_Pavail_variation | Extra robustness | Test model functions when varying available active power. (in EMT model look for oscillations as power varies)
97 | EXT_RfG_MaxPhaseJump_Extreme |  | Test of phase jump robustness, going beyond 20deg (just screening of plant capability) 30deg and 40 deg. (also model robustness)
98 | EXT_RfG_RoCoF_ACER-CurveOF |  | Test of RoCoF robustness, the curve from RfG 2.0 (currently more strict than national requirement)
99 | EXT_RfG_RoCoF_ACER-CurveUF |  | Test of RoCoF robustness, the curve from RfG 2.0 (currently more strict than national requirement)
100 | EXT_RfG_RoCoF+PhaseJump1 |  | Test of robustness, combination of RoCoF and phase jump events
101 | EXT_RfG_RoCoF+PhaseJump2 |  | Test of robustness, combination of RoCoF and phase jump events
102 | EXT_RfG_Fault_3_0_NotDef | Extra faults | Fault simulations with the "not default" Q-mode. Typically voltage control. test of robustness/stability and compliance with PFAPR + reactive fault current
103 | EXT_RfG_Fault_3_20_NotDef |  | -
104 | EXT_RfG_Fault_3_40_NotDef |  | -
105 | EXT_RfG_Fault_3_80_NotDef |  | -
106 | EXT_RfG_Fault_3_thres_NotDef |  | Screening what happens just around FRT threshold - any toggling ?
107 | EXT_RfG_Fault_2_20_NotDef |  | -
108 | EXT_RfG_Fault_2_40_NotDef |  | -
109 | EXT_RfG_Fault_2_80_NotDef |  | -
110 | EXT_RfG_Fault_1_20_NotDef |  | -
111 | EXT_RfG_Fault_1_40_NotDef |  | -
112 | EXT_RfG_Fault_1_80_NotDef |  | -
113 | EXT_RfG_Fault_3_SCR_NotDef |  | Test of plant stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
114 | EXT_RfG_Fault_2_SCR_NotDef |  | Test of plant stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
115 | EXT_RfG_Fault_3_UnderThres_NotDef |  | Test of respons just below FRT threshold in "not default" Q-mode. 3phase fault
116 | EXT_RfG_Fault_3_UnderThres |  | Test of respons just below FRT threshold in default Q-mode. 3phase fault
117 | EXT_RfG_Fault_1_UnderThres |  | Test of respons just below FRT threshold in default Q-mode. 1phase fault
118 | EXT_RfG_Fault_2_double_NotDef |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row. With plant in "not default" Q-mode
119 | EXT_RfG_Fault_double-mix_SCR |  | Test of robustness for consecutive faults - mix of unbalanced/balanced event. First 2 phase then 3 phase faults + grid impedance change in the end.
120 | EXT_RfG_Fault_3_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
121 | EXT_RfG_Fault_2_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
122 | EXT_RfG_Fault_3_ROCOF_curveOF |  | 3phase fault and RoCoF event. Plant stability and model robustness
123 | EXT_RfG_Fault_3_ROCOF_curveUF |  | 3phase fault and RoCoF event. Plant stability and model robustness
124 | EXT_RfG_Fault_3_SCR_freqStep1 |  | 3phase fault, impedance change and frequency steps (frequency back to normal after PPC unfreeze - 6s). Plant stability and model robustness
125 | EXT_RfG_Fault_3_SCR_freqStep2 |  | 3phase fault, impedance change and frequency steps (frequency back to normal before PPC unfreeze - 4s). Plant stability and model robustness
126 | EXT_SCR_step_Max-Min |  | Model robustness - grid impedance change from Max to Min SC. In default Q-mode. Unrealistic case, not used for compliance, but can screen for stability challenges
127 | EXT_SCR_step_Max-Min_NotDef |  | Model robustness - grid impedance change from Max to Min SC. In "not default" Q-mode. Unrealistic case, not used for compliance, but can screen for stability challenges
128 | EXT_RfG_Fault_rec_1_Q |  | Plant stability during faults with critical voltage recovery. (recording from system model simulation). Q-control
129 | EXT_RfG_Fault_rec_1_Q(U) |  | Plant stability during faults with critical voltage recovery. (recording from system model simulation). U-control
130 | EXT_RfG_Fault_rec_1_Q_SCmin |  | - same as above but grid impedance = Min SC instead of controlled source at POC
131 | EXT_RfG_Fault_rec_1_Q(U)_SCmin |  | - same as above but grid impedance = Min SC instead of controlled source at POC
132 | EXT_RfG_Fault_rec_2_Q |  | Recording of double fault in system model. Plant stability in Q-control
133 | EXT_RfG_Fault_rec_2_Q(U) |  | Recording of double fault in system model. Plant stability in U-control
134 | EXT_RfG_Fault_rec_3_Q |  | Recording of fault with very slow voltage recovery. Plant stability in Q-control
135 | EXT_RfG_Fault_rec_3_Q(U) |  | Recording of fault with very slow voltage recovery. Plant stability in U-control
136 | EXT_RfG_proc_VoltageRise_1.2 | Test of protection functionality in model | Testing different overvoltage levels, when will plant trip.
137 | EXT_RfG_proc_VoltageRise_1.3 |  | Important: All simulations in this section is not realistic and so should not be used for plant compliance. However, the protection functionality in the model must be proven, and these simulations is a proposal for that
138 | EXT_RfG_proc_VoltageRise_1.4 |  | -
139 | EXT_RfG_proc_VoltageRise_1.5 |  | -
140 | EXT_RfG_proc_VoltageRise_insta_min |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
141 | EXT_RfG_proc_VoltageRise_insta_max |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
142 | EXT_RfG_proc_Fault_3_0.8pu |  | Test with fault lasting 60seconds, when will plant trip
143 | EXT_RfG_proc_Fault_3_0.6pu |  | -
144 | EXT_RfG_proc_Fault_3_0.40pu |  | -
145 | EXT_RfG_proc_Fault_3_0.20pu |  | -
146 | EXT_RfG_proc_Freq_51.6Hz |  | Test with frequency just above limit, will plant trip ?
147 | EXT_RfG_proc_Freq_47.4Hz |  | Test with frequency just below limit, will plant trip ?
148 | EXT_RfG_proc_Freq_limit_up |  | Test with frequency increasing in steps, when will plant trip ? (does model seem to include all protection functions)
149 | EXT_RfG_proc_Freq_limi_down |  | Test with frequency decreasing in steps, when will plant trip ? (does model seem to include all protection functions)
150 | EXT_RfG_proc_Fault_1_0.05pu | Max 1fase fault current | Test if plant can handle the maximum 1fase fault current. (simulation must be made with HV trafo grounded)

## DCC cases overview
Rank | Name | Category | Comment
1001 | DCC_Fault_3_0 | Faults | Varius fault simulations, how does plant perform ?
1002 | DCC_Fault_3_20 |  | -
1003 | DCC_Fault_3_40 |  | -
1004 | DCC_Fault_3_80 |  | -
1005 | DCC_Fault_2_0 |  | -
1006 | DCC_Fault_2_20 |  | -
1007 | DCC_Fault_2_40 |  | -
1008 | DCC_Fault_2_80 |  | -
1009 | DCC_Fault_1_0 |  | -
1010 | DCC_Fault_1_20 |  | -
1011 | DCC_Fault_1_40 |  | -
1012 | DCC_Fault_1_80 |  | -
1013 | DCC_Fault_3_SCR |  | Fault with impedance change
1014 | DCC_Fault_2_SCR |  | Fault with impedance change
1015 | DCC_SCR_step_Max-Min |  | Changen grid impedance
1016 | DCC_HVRT_profile | Robustness | Increasin voltage in steps - when will plant trip and what is voltage dependence
1017 | DCC_UVRT_profile |  | Decreasing voltage in steps - when will plant trip and what is voltage dependence
1018 | DCC_SystemGuard |  | Test plant/model has SIPS
1019 | DCC_MaxPhaseJump |  | Test plant is compliant with 20deg phase jumps (large jumps)
1020 | DCC_MaxPhaseJump2 |  | Test of phasejump robustness with several consecutive smaller phasejumps adding up to 20deg over 3 periods
1021 | DCC_MaxRoCoF1 |  | Test of robusstness for RoCoF (RoCoF of either 2Hz/s or 0.5Hz/s for long time)
1022 | DCC_MaxRoCoF2 |  | Test of robusstness for RoCoF (RoCoF of either 4Hz/s for just 100ms or 20Hz/s for 20ms.)
1023 | DCC_MaxRoCoF_CurveOF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - over frequency
1024 | DCC_MaxRoCoF_CurveUF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - under frequency
1025 | DCC_LFSM-OU_step1 | Voltage and frequency area | Frequency step changes
1026 | DCC_LFSM-O_ramp |  | Frequency ramp change (over frequency)
1027 | DCC_LFSM-U_ramp |  | Frequency ramp change (under frequency)
1028 | DCC_LFDD |  | Test plant/model has low frequency demand disconnection
1029 | DCC_Faera-O |  | test plant/model performance in full frequency range. (going beyond required frequency range, will plant trip ?)
1030 | DCC_Faera-U |  | test plant/model performance in full frequency range. (going beyond required frequency range, will plant trip ?)
1031 | DCC_Uarea_Qreq_1(up) |  | test plant/model performance in full voltage range
1032 | DCC_Uarea_Qreq_2(up) |  | test plant/model performance in full voltage range
1033 | DCC_Uarea_Qreq_1(down) |  | test plant/model performance in full voltage range
1034 | DCC_Uarea_Qreq_2(down) |  | test plant/model performance in full voltage range
1035 | DCC_Uarea_Qreq_3(down) |  | test plant/model performance in full voltage range
1036 | DCC_VoltageRise_insta_min | Protection | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
1037 | DCC_VoltageDip_insta_min |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
1038 | DCC_freqRise_insta_min |  | test with transient over-frequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
1039 | DCC_freqDip_insta_min |  | test with transient under-frequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).

## Unit cases overview
Rank | Name | Category | Comment
2001 | UNT_SS_flatrun_Q1 | Steady state - model performance/convergence | Test of model performance, flatrun in several operation points and Q-modes
2002 | UNT_SS_flatrun_Q2 |  | -
2003 | UNT_SS_flatrun_Q3 |  | -
2004 | UNT_SS_flatrun_Q4 |  | -
2005 | UNT_SS_flatrun_Q5 |  | -
2006 | UNT_SS_flatrun_Q6 |  | -
2007 | UNT_P_step_up_0.5_0.7 | Active power regulation | Model performance during active power setpoint change
2008 | UNT_Q_control_up | Reactive power regulation | Model performance during Q setpoint change
2009 | UNT_U-Q/Pn_Neutral |  | Model performance during voltage variations
2010 | UNT_fArea | Robustness test / model performance | Test model performance in full frequency area
2011 | UNT_LVFRT_profile |  | Test model performance in LVRT
2012 | UNT_OVRT_profile |  | Test model performance in HVRT
2013 | UNT_Fault_3_0 | Faults | Fault simulations test of robustness/stability
2014 | UNT_Fault_3_20 |  | -
2015 | UNT_Fault_3_40 |  | -
2016 | UNT_Fault_3_80 |  | -
2017 | UNT_Fault_2_0 |  | -
2018 | UNT_Fault_2_20 |  | -
2019 | UNT_Fault_2_40 |  | -
2020 | UNT_Fault_2_80 |  | -
2021 | UNT_Fault_1_0 |  | -
2022 | UNT_Fault_1_20 |  | -
2023 | UNT_Fault_1_40 |  | -
2024 | UNT_Fault_1_80 |  | -
2025 | UNT_Voltage-support |  | Test of reactive fault current contribution, match required static
2026 | UNT_Fault_1_restrike |  | Test of robustness for consecutive faults - single fase with auto reclosure. 2 different faults each with double strike.
2027 | UNT_Fault_3_double |  | Test of robustness for consecutive faults - 3 phase fault, 2 individual faults in a row
2028 | UNT_Fault_2_double |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row
2029 | UNT_Fault_3_20_short |  | Fault simulation with short duration, (just to have case with initially better zoom to inspect)
2030 | UNT_Fault_2_20_short |  | Fault simulation with short duration, (just to have case with initially better zoom to inspect)
2031 | UNT_Fault_3_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
2032 | UNT_Fault_2_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
2033 | UNT_Fault_3_SCR |  | Test of stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
2034 | UNT_Fault_2_SCR |  | Test of stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
2035 | UNT_Fault_3_SCR_freqStep |  | 3phase fault, impedance change and frequency steps. Plant stability and model robustness
2036 | Unit_SCR_step_Max-Min |  | Plant stability / model robustness - grid impedance change from Max to Min SC.
2037 | UNT_MaxPhaseJump | Robustness test / model performance | Test plant is compliant with 20deg phase jumps (large jumps)
2038 | UNT_MaxPhaseJump2 |  | Test of phasejump robustness with several consecutive smaller phasejumps adding up to 20deg over 3 periods
2039 | UNT_MaxRoCoF_CurveOF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - over frequency
2040 | UNT_MaxRoCoF_CurveUF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - under frequency
2041 | UNT_MaxPhaseJump_Extreme_min | Testing of protection functionality in model | Extreme phasejumps with increasing deg. Purpose to provoke large transient current spike. Testing both Protection functionality and model robustness. (min SC level)
2042 | UNT_MaxPhaseJump_Extreme_max |  | Extreme phasejumps with increasing deg. Purpose to provoke large transient current spike. Testing both Protection functionality and model robustness. (max SC level)
2043 | UNT_VoltageRise_1.2 |  | Testing different overvoltage levels, when will plant trip
2044 | UNT_VoltageRise_1.3 |  | -
2045 | UNT_VoltageRise_1.4 |  | -
2046 | UNT_VoltageRise_1.5 |  | -
2047 | UNT_VoltageRise_insta_min |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
2048 | UNT_VoltageRise_insta_max |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
2049 | Unit_freqRise_insta_min |  | test with transient over-frequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
2050 | Unit_freqDip_insta_min |  | test with transient under-frequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
2051 | UNT_prot_Fault_3_0.8pu |  | Test with fault lasting 60seconds, when will plant trip
2052 | UNT_prot_Fault_3_0.6pu |  | -
2053 | UNT_prot_Fault_3_0.40pu |  | -
2054 | UNT_prot_Fault_3_0.20pu |  | -
2055 | UNT_prot_Fault_1_0.05pu |  | -
2056 | UNT_Freq_53Hz |  | Test with frequency just above limit, will plant trip ?
2057 | UNT_Freq_46Hz |  | Test with frequency just below limit, will plant trip ?
2058 | UNT_Freq_limit_up |  | Test with frequency increasing in steps, when will plant trip ? (does model seem to include all protection functions)
2059 | UNT_Freq_limi_down |  | Test with frequency decreasing in steps, when will plant trip ? (does model seem to include all protection functions)
2060 | UNT_Pavail_variation | Variation of available power | Can model handle variation in active power ?

## datavalidation (hidden)
DK1 | Q | No P(f) | Max | TRUE | RfG
DK2 | Q(U) | LFSM | Min | FALSE | DCC
| PF | FSM | Tuning |  | Unit
| Default | LFSM+FSM | Ideal |  | Custom
| Qmode3 | Pmode4
| Qmode4 | Pmode5
| Qmode5 | Pmode6
| Qmode6 | Pmode7