## Input
Input model-specific information here: | Pn (MW) | Sb (MVA) | Vn_PoC (kV) | SCR | X/R | droop (%) | Qmode_Q | Qmode_V | Qmode_PF | ProjectName | PSCAD compiler | PSCAD TimeStep (us) | TotalCases | Volley
| 10 | 10 | 62.5 | 5 | 15 | 2 | 0 | 1 | 2 | Fredericia | Intel(R) Visual Fortran Compiler XE 15.0.1.148 | 2 | 32 | 8
[7 empty] | Note: |  |  |  | See 'PSCAD Compliers' sheet for guidance |  |  | The number of simulations that are run in parallel
Input the specific number specified by the model developer for different reactive power control modes in columns 'Qmode_Q', 'Qmode_V' and 'Qmode_PF'
Qmode_Q: Reactive power reference control
Qmode_V: Voltage control
Qmode_PF: Power factor control

## Cases
ION | TestType | Rank | Included | P0 | Qmode | InitValue | PrefCtrl | QrefCtrl | FaultType | FaultDepth | FaultPeriod | VSPhaseCtrl | VSVoltCtrl | VSFreqCtrl | GridImped | Tstop (s) | C1start | C1setpoint | C1ramp | C2start | C2setpoint | C2ramp | C3start | C3setpoint | C3ramp | C4start | C4setpoint | C4ramp | C5start | C5setpoint | C5ramp | C6start | C6setpoint | C6ramp | C7start | C7setpoint | C7ramp
3.4.3.2 | Fault_3_0pu | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0.01 | 0.15 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.2 | Fault_3_0.2pu | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0.2 | 0.45 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.3 | Fault_2_0pu | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 1e-06 | 0.15 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.3 | Fault_2_0.2pu | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 0.2 | 0.45 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.4 | Fault_1_0pu | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1e-06 | 0.15 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.4 | Fault_1_0.2pu | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0.2 | 0.45 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.2 | Fault_3_0.4pu | 7 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0.4 | 0.75 | 0 | 0 | 0 | 1 | 4.5 | 3 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.3 | Fault_2_0.4pu | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 0.4 | 0.75 | 0 | 0 | 0 | 1 | 4.5 | 3 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.4 | Fault_1_0.4pu | 9 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0.4 | 0.75 | 0 | 0 | 0 | 1 | 4.5 | 3 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.5 | VoltSupport | 10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1e-06 | 4.5 | 3 | 0.7 | 0 | 3.2 | 0.5 | 0 | 3.4 | 0.3 | 0 | 3.6 | 1 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.2.1 | MaxPhaseJump | 11 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 5 | 3 | 20 | 0 | 3.5 | 0 | 0 | 4 | -20 | 0 | 4.5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.2 | Fault_3_0.8pu | 12 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0.8 | 1.35 | 0 | 0 | 0 | 1 | 5 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.2 | Fault_3_0.85pu | 13 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0.85 | 1.35 | 0 | 0 | 0 | 1 | 5 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.3 | Fault_2_0.8pu | 14 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 0.8 | 1.35 | 0 | 0 | 0 | 1 | 5 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.4 | Fault_1_0.8pu | 15 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0.8 | 1.35 | 0 | 0 | 0 | 1 | 5 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3.1 | FRTcurve | 16 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1e-06 | 6.5 | 3 | 0.15 | 0 | 3.25 | 0.15 | 0.6 | 4.5 | 0.9 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.4.1 | MaxRoCoF | 17 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 10 | 3 | 50 | -2 | 4.25 | 47.5 | 2 | 5.5 | 50 | 2 | 6.25 | 51.5 | -2 | 7 | 50 | 0 | 10 | 0 | 0 | 0 | 0 | 0
3.2.3.2 | LFSM-O_ramp | 18 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 18 | 3 | 50 | 0.5 | 6 | 51.5 | 0 | 8 | 51.5 | -0.2 | 14.5 | 50.2 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.3.2 | LFSM-U_ramp | 19 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 18 | 3 | 50 | -0.5 | 6 | 48.5 | 0 | 8 | 48.5 | 0.2 | 14.5 | 49.8 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.4.1 | U-Q/Pmax_NegQ | 20 | 1 | 1 | 0 | -0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1e-06 | 30 | 3 | 1 | 0 | 10 | 1.05 | 0 | 17 | 0.96 | 0 | 24 | 1 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.4.1 | U-Q/Pmax_PosQ | 21 | 1 | 1 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1e-06 | 30 | 3 | 1 | 0 | 10 | 1.04 | 0 | 17 | 0.91 | 0 | 24 | 1 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.1.1 | VoltCtrlMode | 22 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 52 | 3 | 1.0317 | 0 | 10 | 0.98167 | 0 | 17 | 1.0067 | 0 | 24 | 1.0567 | 0 | 31 | 1.0067 | 0 | 38 | 0.95667 | 0 | 45 | 1.0067 | 0
3.2.1.1 | P_step_down_0.7_0.5 | 23 | 1 | 0.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 80 | 3 | 0.5 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1.1 | P_step_up_0.5_0.7 | 24 | 1 | 0.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 80 | 3 | 0.7 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.2.1 | FSM | 25 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 80 | 3 | 50.19 | 0 | 22 | 50 | 0 | 42 | 49.81 | 0 | 62 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.3.1 | LFSM-O&U_setpoint | 26 | 1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 80 | 3 | 51.49 | 0 | 22 | 50 | 0 | 42 | 48.51 | 0 | 62 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1.1 | P_step_down_1_0.7 | 27 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 3 | 0.7 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1.1 | P_step_up_0.7_1 | 28 | 1 | 0.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 3 | 1 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.3.1 | PFCtrlMode | 29 | 1 | 0.3 | 2 | 0.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 140 | 3 | 0.4 | 0 | 35 | 0.5 | 0 | 70 | 0.6 | 0 | 105 | 0.7 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.2.1 | Q_step_down | 30 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 145 | 3 | -0.1 | 0 | 40 | -0.2 | 0 | 75 | -0.3 | 0 | 110 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.2.1 | Q_step_up | 31 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 145 | 3 | 0.1 | 0 | 40 | 0.2 | 0 | 75 | 0.3 | 0 | 110 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1.1 | P_step_up_0_0.5 | 32 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 155 | 3 | 0.5 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.9.9.9 | PF_test | 33 | 1 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 3 | 0.9 | 0 | 10 | -0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## PSCAD Compliers
GFortran 4.6.2
GFortran 8.1
GFortran 8.1 (64-bit)
Intel(R) Visual Fortran Compiler XE 12.1.7.371
Intel(R) Visual Fortran Compiler XE 15.0.1.148
Intel(R) Visual Fortran Compiler XE 15.0.1.148 (64-bit)
Intel(R) Visual Fortran Compiler XE 15.0.5.280
Intel(R) Visual Fortran Compiler XE 15.0.5.280 (64-bit)